## Answers
id | Gov | ROU | Sub_zone_N | Source | P_Zone | Elev_min | Elev_Max | To_check | check_answ | Ask_Oper | P_Zone_new | P_zone_ver | P_Zone_change
72 | Mafraq | North Badia | Hashmyye/Alyah shwee'er/ Manshiyyet khaleefa /slaah JAW | K140 PS | Safawi_PS | 775 | 820 | CHECK the pressure zone - if K140 or Safawi ? are theses two facilities connected ? | K140_PS (not Safawi). K140 PS lies inside this zone, Safawi PS ~25 km away. Area tapped DN100/63 on DN400 main from wells K136+K140 (YWC src: wells 136+140, Safawi WS) - same system, pressure from K140 side. | No | K140_PS | 0 | Yes
74 | Mafraq | North Badia | Dir Al-Kahf | Beshryyeh PS | Bishiryyah_PS | 990 | 1067 | TO CHECK IF FROM Beshryyeh PS or Dir Al kahf PS ? | Beshryyeh PS - keep Bishiryyah_PS. Field: DN200 from Beshryyeh PS (main filling Dir Al-Kahf tank). Dir Al-Kahf PS sits in this zone (990-1067m) but its pumps H=250m serve upper villages (id75). YWC names Dair Al Kahef PS | Confirm | Bishiryyah_PS | 0
75 | Mafraq | North Badia | Tal Rmah,Mrajb, deir al qen ,jadaa,Mathnah , mansoora | Dr Al-kahf PS | Dir Al-kahf PS | 1071 | 1174 | Check if the resv Dair Al Qenn is used ? or bypassed ? if used how ? | Dair Al Qenn Resv NOT used - bypassed (Master plan: Dir Al-Qun Resv = Abandoned). Fed directly by DN150 from Dir Al-Kahf PS (YWC confirms). YWC has 2 schedules: Tal Rmah / Deir Al Qen+Jadaa+Mathnah+Mansoora | No | Dir Al-kahf PS | 1
97 | Mafraq | North Badia | Koum Ahmar Hay shamali and Janoobi | Koum Ahmar ps | Koum Ahmar_PS | 696 | 750 | How many discharge lines ? split the hydraulic zone | Koum Ahmar PS has 2 pumps (50m3/h@250m, 100m3/h@100m) and 2 distribution outlets DN125 + DN100 (field notes). This zone fed by DN125 (+DN100) -> Koum Ahmar_PS_125. Confirm which pump feeds which line. | Confirm | Koum Ahmar_PS_125 | 0 | Yes
98 | Mafraq | North Badia | MANSHIYYET ALKAMEES | Koum Ahmar ps | Koum Ahmar_PS | 727 | 761 | How many discharge lines ? split the hydraulic zone | Koum Ahmar PS has 2 pumps (50m3/h@250m, 100m3/h@100m) and 2 distribution outlets DN125 + DN100 (field notes). This zone fed by DN100 -> Koum Ahmar_PS_100. Confirm which pump feeds which line. | Confirm | Koum Ahmar_PS_100 | 0 | Yes
99 | Mafraq | North Badia | Rasm Alhesan | Koum Ahmar ps | Koum Ahmar_PS | 744 | 766 | How many discharge lines ? split the hydraulic zone | Koum Ahmar PS has 2 pumps (50m3/h@250m, 100m3/h@100m) and 2 distribution outlets DN125 + DN100 (field notes). This zone fed by DN100 -> Koum Ahmar_PS_100. Confirm which pump feeds which line. | Confirm | Koum Ahmar_PS_100 | 0 | Yes
100 | Mafraq | North Badia | Hay Al Joulan | Koum Ahmar ps | Koum Ahmar_PS | 702 | 720 | How many discharge lines ? split the hydraulic zone | Koum Ahmar PS has 2 pumps (50m3/h@250m, 100m3/h@100m) and 2 distribution outlets DN125 + DN100 (field notes). Zone fed by DN100 (+DN50) -> Koum Ahmar_PS_100. GIS network differs - update. | Confirm | Koum Ahmar_PS_100 | 0 | Yes
316 | Mafraq | Mafraq | Bweidha_Gharbiyeh | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | 857 | 915 | Check if really they by-pass the reservoir of Bweidha | NO bypass here: fed by DN100 DISCHARGE from Bweidha PS (field notes), YWC: BWAIDAH PS. Change P_Zone to Bweidha_PS_100. | No | Bweidha_PS_100 | 0 | Yes
317 | Mafraq | Mafraq | Bweidha_Oleimath | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | 828 | 878 | Check if really they by-pass the reservoir of Bweidha | Yes - bypass confirmed: DN150 tapped on DN300 bypassing Bweidha Resv (1 bar) + DN100 from Bweidha PS discharge (double feed). YWC: UM LOLO PS (DN300 = Um Lulu PS water). Keep BYPASS. | Confirm | Bweidha_Resv_BYPASS | 0
318 | Mafraq | Mafraq | Abu_Khalaf | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | 836 | 892 | Check if really they by-pass the reservoir of Bweidha | Yes - bypass confirmed: fed by DN300 bypassing Bweidha Resv (residual 1 bar). YWC source = UM LOLO PS, i.e. water comes directly from Um Lulu PS through DN300. Keep Bweidha_Resv_BYPASS. | No | Bweidha_Resv_BYPASS | 1
319 | Mafraq | Mafraq | sahah | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | 815 | 861 | Check if really they by-pass the reservoir of Bweidha | Yes - bypass confirmed: fed by DN300 bypassing Bweidha Resv (residual 1 bar). YWC source = UM LOLO PS, i.e. water comes directly from Um Lulu PS through DN300. Keep Bweidha_Resv_BYPASS. | No | Bweidha_Resv_BYPASS | 1
320 | Mafraq | Mafraq | RHAb | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | 782 | 906 | Check if really they by-pass the reservoir of Bweidha | Yes - bypass confirmed: 2 x DN200 taps on DN300 bypassing Bweidha Resv (1 bar), 12 valves split zone 6-8h each. YWC: BWAIDAH PS. Keep Bweidha_Resv_BYPASS. | No | Bweidha_Resv_BYPASS | 1
321 | Mafraq | Mafraq | Al_Qadam | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | 827 | 901 | Check if really they by-pass the reservoir of Bweidha | Yes - bypass confirmed: DN100 tapped on DN300 bypassing Bweidha Resv, but this line is OUT OF SERVICE (field). Qadam Resv = Abandoned (MP). Ask operator current supply. | Yes | Bweidha_Resv_BYPASS | 0
322 | Mafraq | Mafraq | Ein_Bani_Hassan | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | 624 | 890 | Check if really they by-pass the reservoir of Bweidha | Yes - bypass confirmed: DN200 branch next to Qadam Resv; Qadam Resv is Abandoned (MP) so the line is not re-stored. YWC: BWAIDAH PS. Keep BYPASS; update GIS: DN200 Qadam->Maamaria. | No | Bweidha_Resv_BYPASS | 1
323 | Mafraq | Mafraq | Mamarieyh | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | 656 | 791 | Check if really they by-pass the reservoir of Bweidha | Yes - bypass confirmed: DN200 branch next to Qadam Resv; Qadam Resv is Abandoned (MP) so the line is not re-stored. YWC: BWAIDAH PS. Keep BYPASS; update GIS: DN200 Qadam->Maamaria. | No | Bweidha_Resv_BYPASS | 1
324 | Mafraq | Mafraq | Hamamt_Omoush | Bweidha_Resv_PS | Bweidha_Resv_300_G | 769 | 860 | Check from where it's fed Bwaida_Reservoir_300_gravity or Rehab_Resv ? | Fed from Bweidha DN300 (DN150 tapped on DN300, no connections on DN150) - NOT Rehab: Rhab PS is 60m3/h@300m booster with 25m3 tank. YWC: BWAIDAH PS. Keep Bweidha_Resv_300_G. | No | Bweidha_Resv_300_G | 1
325 | Mafraq | Mafraq | Hamamt-Monkhadat | Bweidha_Resv_PS | Bweidha_Resv_300_G | 769 | 844 | Check from where it's fed Bwaida_Reservoir_300_gravity or Rehab_Resv ? | Fed from Bweidha DN300 (DN150 tapped on DN300, no connections on DN150) - NOT Rehab: Rhab PS is 60m3/h@300m booster with 25m3 tank. YWC: BWAIDAH PS. Keep Bweidha_Resv_300_G. | No | Bweidha_Resv_300_G | 1
326 | Mafraq | Mafraq | Hamamt-Alimat | Bweidha_Resv_PS | Bweidha_Resv_300_G | 760 | 861 | Check from where it's fed Bwaida_Reservoir_300_gravity or Rehab_Resv ? | Fed from Bweidha DN300 (DN150 tapped on DN300, no connections on DN150) - NOT Rehab: Rhab PS is 60m3/h@300m booster with 25m3 tank. YWC: BWAIDAH PS. Keep Bweidha_Resv_300_G (DN125 on DN150). | No | Bweidha_Resv_300_G | 1
327 | Mafraq | Mafraq | Dogmosseh | Dogmseh_PS | Dogmseh_PS | 736 | 851 | Check if fed from Dogmseh_PS or Bweida_PS | Dogmseh_PS. YWC: DOGMOSEH PS. Dogmseh PS (2 pumps 50m3/h@400m/@250m, 4x25m3 tanks) is fed from Bweidha system; zone boosted by Dogmseh PS 4h for high points (DN125 from DN150). Keep Dogmseh_PS. | No | Dogmseh_PS | 1
328 | Mafraq | Mafraq | Nadrah | Dogmseh_PS | Dogmseh_PS | 763 | 819 | Check if fed from Dogmseh_PS or Bweida_PS | Dogmseh_PS. YWC: DOGMOSEH PS. Dogmseh PS (2 pumps 50m3/h@400m/@250m, 4x25m3 tanks) is fed from Bweidha system; zone boosted by Dogmseh PS 4h for high points (DN100 from DN150). Keep Dogmseh_PS. | No | Dogmseh_PS | 1
329 | Mafraq | Mafraq | Medwar | Bweidha_Resv_PS | Bweidha_Resv_300_G | 712 | 773 | Check from where it's fed Bwaida_Reservoir_300_gravity or Rehab_Resv ? | Neither Bweidha nor Rehab: YWC lists MEDWAR under QNAYYA PS (Qnayya WS). Nearest zones Khatla/Dahal = Al-Qnaya_PS DN150->DN100, field: DN100 continues south. Change to Al-Qnaya_PS - confirm. | Confirm | Al-Qnaya_PS | 0 | Yes
357 | Mafraq | Mafraq | Ghadeer | Za'tary | Zaatary_PS_400 | 641 | 676 | Check if fed from Zaatary_PS or Sumaya_PS or Hayan_booster | Zaatary_PS_400 (confirmed). DN200 tapped on Zaatari DN400 discharge next to Hayyan PS. YWC: HAYYAN BOOSTER/ZAATARI PS - booster is downstream on same line; zone takes Zaatari DN400 pressure. | No | Zaatary_PS_400 | 1
358 | Mafraq | Mafraq | Hay_Kwaytiyeh | Za'tary | Zaatary_PS_400 | 660 | 707 | Check if fed from Zaatary_PS or Sumaya_PS or Hayan_booster | Zaatary_PS_400 (confirmed). DN100 + direct connections on Zaatari DN400 discharge before Hayyan PS. YWC: HAYYAN BOOSTER/ZAATARI PS - zone takes Zaatari DN400 pressure. | No | Zaatary_PS_400 | 1
369 | Mafraq | Mafraq | Al-Hudud jaber | Jaber | Jaber_Resv | 571 | 598 | is this area fed by the Reservoir Hudud or by Jaber PS ? | Hudud Reservoir (gravity). Reservoir lies inside this zone and is filled by DN100 from Jaber PS; network fed from Resv (field). YWC: HODOOD RES. Keep Jaber_Resv (better: Hudud_Jaber_Resv). MP: access needs permit. | No | Jaber_Resv | 1
387 | Mafraq | Mafraq | HAY ALZHOR SHARQI , SHARI ALMOHNDISIN | Sumaya | Sumaya PS_400 | 689 | 727 | Check if fe from Sumaya_PS or Hayyan_Booster ? | Sumaya PS (not Hayyan booster). YWC: SUMAYYA PS; field notes: direct from Sumaya DN400 line -> DN200 -> DN150 branches. Hayyan booster is 20 m away but not feeding. Keep Sumaya PS_400. | No | Sumaya PS_400 | 1
388 | Mafraq | Mafraq | HAY NOWWARA , HAY MAQAM , HAY ALHOSBAN , HAY ALZHOR QARBI, SHARI ALMOHNDISIN | Sumaya | Sumaya PS_400 | 687 | 731 | Check if fe from Sumaya_PS or Hayyan_Booster ? | Sumaya PS (not Hayyan booster). YWC: SUMAYYA PS; field notes: direct from Sumaya DN400 line (DN400/500) -> DN150/125 branches. Keep Sumaya PS_400. | No | Sumaya PS_400 | 1
389 | Mafraq | Mafraq | Hay AL HUSSEIN AND HAY FDAIN AND PART OF HAY ALTHOBAT AND HAY JEA'A | Sumaya | Sumaya PS_400 | 664 | 711 | Check if fed from Sumaya_PS or Hayyan_Booster ? | Sumaya PS (not Hayyan booster). YWC: SUMAYYA PS; field notes: direct from Sumaya DN400 line (DN400/500) -> DN150/125 branches. Hayyan booster is next to zone but not feeding. Keep Sumaya PS_400. | No | Sumaya PS_400 | 1
390 | Mafraq | Mafraq | HAY JANOOBI AND DAHEYT KING ABDULLAH AND ESKAN | Sumaya | Sumaya PS_400 | 658 | 707 | Check if fe from Sumaya_PS or Hayyan_Booster ? | Sumaya PS (not Hayyan booster). YWC: SUMAYYA PS; field notes: direct from Sumaya DN400 line reduced to DN200 -> DN150/125. Keep Sumaya PS_400. | No | Sumaya PS_400 | 1
391 | Mafraq | Mafraq | SOOQ HAY THOBBAT AND STREET OF JAISH | Sumaya PS | Sumaya PS_400 | 661 | 698 | Check if fe from Sumaya_PS or Hayyan_Booster ? | Sumaya PS (not Hayyan). YWC: SUMAYYA PS. But field notes: separate DN200 direct from Sumaya PS -> DN150 -> DN125, not the DN400 line. Change to Sumaya PS_200. | Confirm | Sumaya PS_200 | 0 | Yes
398 | Mafraq | Mafraq | Um karouba | bwida gravity | Bweidha_Resv_300_G | 745 | 823 | Check from where it's fed Bwaida_Reservoir_300_gravity or Rehab_Resv ? | Bweidha DN300 - NOT Rehab. Field: DN63/100 from DN150 on DN300 from Bweidha PS, fed from the north. YWC: HAMAMT OMOUSH / BWAIDAH PS. Rhab PS is only a 60m3/h@300m booster. Keep Bweidha_Resv_300_G. | No | Bweidha_Resv_300_G | 1
399 | Mafraq | Mafraq | mozareen Daqmaseh | Dogmseh_PS | Dogmseh_PS | 719 | 795 | Check if fed from Dogmseh_PS or Bweida_PS | Dogmseh_PS. YWC: DOGMOSEH PS. Dogmseh PS (2 pumps 50m3/h@400m/@250m, 4x25m3 tanks) is fed from Bweidha system; zone boosted by Dogmseh PS; PS is inside this zone. Keep Dogmseh_PS. | No | Dogmseh_PS | 1
413 | Mafraq | Mafraq | Hay aljeeran | Al Zubaideyeh PS | Al Zubaideyeh_PS | 659 | 683 | 2 discharge pipes ? if yes split the hydraulic zone | Yes, Zubaidiyeh PS has >1 discharge: 2 pumps (50m3/h@100m, 100m3/h@150m) + DN150/DN125/DN100 outlets (field). This zone: DN100 direct from PS -> Al Zubaideyeh_PS_100. | Confirm | Al Zubaideyeh_PS_100 | 0 | Yes
414 | Mafraq | Mafraq | hay abushakir | Al Zubaideyeh PS | Al Zubaideyeh_PS | 658 | 668 | 2 discharge pipes ? if yes split the hydraulic zone | Yes, Zubaidiyeh PS has >1 discharge: 2 pumps (50m3/h@100m, 100m3/h@150m) + DN150/DN125/DN100 outlets (field). This zone: DN150 from PS -> Al Zubaideyeh_PS_150. | Confirm | Al Zubaideyeh_PS_150 | 0 | Yes
415 | Mafraq | Mafraq | Hay zarafat | Al Zubaideyeh PS | Al Zubaideyeh_PS | 663 | 675 | 2 discharge pipes ? if yes split the hydraulic zone | Yes, Zubaidiyeh PS has >1 discharge: 2 pumps (50m3/h@100m, 100m3/h@150m) + DN150/DN125/DN100 outlets (field). This zone: DN125 PE from PS -> Al Zubaideyeh_PS_125. | Confirm | Al Zubaideyeh_PS_125 | 0 | Yes
416 | Mafraq | Mafraq | Fhailyyeh | Al Zubaideyeh PS | Al Zubaideyeh_PS | 662 | 680 | 2 discharge pipes ? if yes split the hydraulic zone | Yes, Zubaidiyeh PS has >1 discharge: 2 pumps (50m3/h@100m, 100m3/h@150m) + DN150/DN125/DN100 outlets (field). This zone: DN125 from PS -> Al Zubaideyeh_PS_125. | Confirm | Al Zubaideyeh_PS_125 | 0 | Yes
417 | Mafraq | Mafraq | Hay Nada Zbadi | Al Zubaideyeh PS | Al Zubaideyeh_PS | 660 | 678 | 2 discharge pipes ? if yes split the hydraulic zone | Yes, Zubaidiyeh PS has >1 discharge: 2 pumps (50m3/h@100m, 100m3/h@150m) + DN150/DN125/DN100 outlets (field). This zone: DN125 from PS -> Al Zubaideyeh_PS_125. | Confirm | Al Zubaideyeh_PS_125 | 0 | Yes
418 | Mafraq | Mafraq | Tareeq Al Nahdah | Al Zubaideyeh PS | Al Zubaideyeh_PS | 653 | 680 | 2 discharge pipes ? if yes split the hydraulic zone | Yes, Zubaidiyeh PS has >1 discharge: 2 pumps (50m3/h@100m, 100m3/h@150m) + DN150/DN125/DN100 outlets (field). This zone: DN150 from PS -> Al Zubaideyeh_PS_150. | Confirm | Al Zubaideyeh_PS_150 | 0 | Yes
419 | Mafraq | Mafraq | Hwajah and Hay alamerah Hya | Al Zubaideyeh PS | Al Zubaideyeh_PS | 636 | 671 | 2 discharge pipes ? if yes split the hydraulic zone | Yes, Zubaidiyeh PS has >1 discharge: 2 pumps (50m3/h@100m, 100m3/h@150m) + DN150/DN125/DN100 outlets (field). This zone: DN100 from PS -> Al Zubaideyeh_PS_100. | Confirm | Al Zubaideyeh_PS_100 | 0 | Yes
420 | Mafraq | Mafraq | Hay Albaladiyyeh | Um EsSerb PS | Um EsSerb PS | 642 | 654 | is there 2 discharge from the PS 100 + 150 ? PS Um-Serb PS feed Zubeydeh PS or invers ? | Yes, 2 discharges: DN100 + DN150 (field notes; pumps 100m3/h@150m + 50m3/h@200m). Direction Um Serb<->Zubaidiyeh unknown (both Zaatari WS) - ask operator. Zone on DN100 -> Um EsSerb PS_100 | Yes | Um EsSerb PS_100 | 0 | Yes
421 | Mafraq | Mafraq | Al wasit and tareeq samp alsarhan | Um EsSerb PS | Um EsSerb PS | 645 | 663 | is there 2 discharge from the PS 100 + 150 ? PS Um-Serb PS feed Zubeydeh PS or invers ? | Yes, 2 discharges: DN100 + DN150 (field notes; pumps 100m3/h@150m + 50m3/h@200m). Direction Um Serb<->Zubaidiyeh unknown (both Zaatari WS) - ask operator. Zone on DN150 -> Um EsSerb PS_150 | Yes | Um EsSerb PS_150 | 0 | Yes
422 | Mafraq | Mafraq | Rawded Rowayei | Um EsSerb PS | Um EsSerb PS | 646 | 669 | is there 2 discharge from the PS 100 + 150 ? PS Um-Serb PS feed Zubeydeh PS or invers ? | Yes, 2 discharges: DN100 + DN150 (field notes; pumps 100m3/h@150m + 50m3/h@200m). Direction Um Serb<->Zubaidiyeh unknown (both Zaatari WS) - ask operator. Zone on separate DN100 -> Um EsSerb PS_100 | Yes | Um EsSerb PS_100 | 0 | Yes
423 | Mafraq | Mafraq | Sawalah | Um EsSerb PS | Um EsSerb PS | 642 | 667 | is there 2 discharge from the PS 100 + 150 ? PS Um-Serb PS feed Zubeydeh PS or invers ? | Yes, 2 discharges: DN100 + DN150 (field notes; pumps 100m3/h@150m + 50m3/h@200m). Direction Um Serb<->Zubaidiyeh unknown (both Zaatari WS) - ask operator. Zone on separate DN100 -> Um EsSerb PS_100 | Yes | Um EsSerb PS_100 | 0 | Yes
424 | Mafraq | Mafraq | Nahdah | Um EsSerb PS | Um EsSerb PS | 650 | 675 | is there 2 discharge from the PS 100 + 150 ? PS Um-Serb PS feed Zubeydeh PS or invers ? | Yes, 2 discharges: DN100 + DN150 (field notes; pumps 100m3/h@150m + 50m3/h@200m). Direction Um Serb<->Zubaidiyeh unknown (both Zaatari WS) - ask operator. Zone on DN150 -> Um EsSerb PS_150 | Yes | Um EsSerb PS_150 | 0 | Yes
439 | Mafraq | Mafraq | Jabal anoor phase 1 | Balaama PS | Balaama_PS | 655 | 711 | check if fed by DN200 from Balaama Resv by gravity ? or from Znayah PS ? | Balaama Resv by gravity (DN200), not Znayah PS. YWC: 'Balaam Res (By Gravity)' for Balaama Phase 1 + Hay Al Hussein. Balaama tank 1000m3 is 220 m away (pumps only H=70m). Change to Balaama_Resv_200_G. | No | Balaama_Resv_200_G | 0 | Yes
447 | Mafraq | Mafraq | Hay AGGAD and Balaama Hay shamali | Zeenah PS | Znayah_PS_200 | 650 | 763 | check if fed by DN200 from Balaama Resv by gravity ? or from Znayah PS_DN200 ? | Mixed - split polygon: Hay Aggad = Balaama Resv gravity (YWC 62%), Balaama Hay Shamali = Znayah PS (YWC 33%). Field: DN200 from PS with DN125 branches. Keep Znayah_PS_200 for north part; confirm split line. | Confirm | Znayah_PS_200 + Balaama_Resv_200_G | 0 | Yes
448 | Mafraq | Mafraq | Mortafaat Balaama (Jabal alnaar old netowrk) | Zeenah PS | Znayah_PS_200 | 664 | 710 | check if fed by DN200 from Balaama Resv by gravity ? or from Znayah PS_DN200 ? | Znayah PS DN200 (not Balaama gravity). YWC: MORTAFAAT BALAAMA / Znayyah PS; high area; field: DN100 from DN200 from PS. Keep Znayah_PS_200. | No | Znayah_PS_200 | 1
454 | Mafraq | Mafraq | Baej Hay Janoobi Gharbi | BAEJ 2 PS | BAEJ 2_PS | 662 | 681 | Check if really from Baaj_PS_2 ? how many discharge lines ? if more then 1 split the hydraulic zone. | Yes, BAEJ 2 PS (YWC confirms, 2 pumps 100m3/h@150m). 2 outlets DN150 + DN100 -> split. This zone: DN150 direct -> BAEJ 2_PS_150. | Confirm | BAEJ 2_PS_150 | 0 | Yes
455 | Mafraq | Mafraq | BAEJ HAY JANOOBI | BAEJ 2 PS | BAEJ 2_PS | 659 | 679 | Check if really from Baaj_PS_2 ? how many discharge lines ? if more then 1 split the hydraulic zone. | Yes, BAEJ 2 PS (YWC confirms, 2 pumps 100m3/h@150m). 2 outlets DN150 + DN100 -> split. This zone: DN100->50 direct -> BAEJ 2_PS_100. | Confirm | BAEJ 2_PS_100 | 0 | Yes
456 | Mafraq | Mafraq | Baej Hay Gharbi | BAEJ 2 PS | BAEJ 2_PS | 666 | 678 | Check if really from Baaj_PS_2 ? how many discharge lines ? if more then 1 split the hydraulic zone. | Yes, BAEJ 2 PS (YWC confirms, 2 pumps 100m3/h@150m). 2 outlets DN150 + DN100 -> split. This zone: DN100 -> BAEJ 2_PS_100. | Confirm | BAEJ 2_PS_100 | 0 | Yes
457 | Mafraq | Mafraq | Baej Hay SHAMALI | BAEJ 2 PS | BAEJ 2_PS | 669 | 685 | Check if really from Baaj_PS_2 ? how many discharge lines ? if more then 1 split the hydraulic zone. | Yes, BAEJ 2 PS (YWC confirms, 2 pumps 100m3/h@150m). 2 outlets DN150 + DN100 -> split. This zone: collector valve DN50/25 -> BAEJ 2_PS_100 (confirm which outlet). | Confirm | BAEJ 2_PS_100 | 0 | Yes
458 | Mafraq | Mafraq | Hay Al Mebrek and Hay al ATHAR | BAEJ 2 PS | BAEJ 2_PS | 672 | 691 | Check if really from Baaj_PS_2 ? how many discharge lines ? if more then 1 split the hydraulic zone. | Yes, BAEJ 2 PS (YWC confirms, 2 pumps 100m3/h@150m). 2 outlets DN150 + DN100 -> split. This zone: main line + DN100 to Mebrek -> BAEJ 2_PS_100. | Confirm | BAEJ 2_PS_100 | 0 | Yes
459 | Mafraq | Mafraq | BEDAYAT TAREEQ MESHIREF | BAEJ 3 PS | BAEJ 3_PS | 667 | 684 | To check with operator if realy from Baaj PS 3 ? how many discharge ? | Yes, BAEJ 3 PS (YWC confirms; PS inside zone 459). 1 pump 50m3/h@100m, outlets are DN100 from the same collector = same head -> no split needed. | No | BAEJ 3_PS | 1
460 | Mafraq | Mafraq | Mehrif Hay shamali | BAEJ 3 PS | BAEJ 3_PS | 672 | 700 | To check with operator if realy from Baaj PS 3 ? how many discharge ? | Yes, BAEJ 3 PS (YWC confirms; PS inside zone 459). 1 pump 50m3/h@100m, outlets are DN100 from the same collector = same head -> no split needed. | No | BAEJ 3_PS | 1
461 | Mafraq | Mafraq | Hosha | Hosha_Booster | Hosha_Booster_150 | 619 | 735 | Fed by Hosha booster ? or um Lulu ps ? | Hosha Booster (not Um Lulu PS pumps). Um Lulu Resv feeds the booster by gravity DN200, booster (2 pumps) feeds zone. YWC: 'UM LOLO GRAVITY TO BOOSTER HOSHA'. Hosha Resv abandoned. Keep Hosha_Booster_150. | No | Hosha_Booster_150 | 1
462 | Mafraq | Mafraq | Hamnanah , Bostanah and part of Um SWEIneh | Balama PS | Znayah_PS_200 | 641 | 707 | check if fed by DN200 from Balaama Resv by gravity ? or from Znayah PS_DN200 ? | Znayah PS (not Balaama gravity). YWC: HAMNANAH+BOSTANAH+UM SWEINEH / Znayyah PS. Field: DN180 + DN300 from PS -> may be Znayah_PS_300_1 rather than _200; confirm which line. | Confirm | Znayah_PS_300_1 | 0 | Yes
493 | Jarash | Jarash | Hay kalieel | Boidah Ps to resv | Bowidah_PS | 732 | 883 | To check P_Zone : Balela Reservoir instead of Bowidah_PS | Yes - change to Balela Resv (gravity). Bowidah PS pumps to Balela Resv; field: gravity DN100 from DN150 from Balela Resv. Change to Balela_Resv (not in YWC Mafraq layer). | No | Balela_Resv | 0 | Yes
611 | Irbid | Ramtha | Hay bareed bwaidah | Hosha_Booster | Hosha_Booster_200 | 562 | 598 | Fed by Hosha booster or Um Lulu PS ? | Hosha Booster (not Um Lulu PS pumps). Um Lulu Resv feeds the booster by gravity DN200, booster DN200 discharge feeds Bwaidha. YWC: 'UM LOLO GRAVITY TO HOSHA BOOSTER'. Keep Hosha_Booster_200. | No | Hosha_Booster_200 | 1
612 | Irbid | Ramtha | Hay mesmar | Hosha_Booster | Hosha_Booster_200 | 558 | 576 | Fed by Hosha booster or Um Lulu PS ? | Hosha Booster (not Um Lulu PS pumps). Um Lulu Resv feeds the booster by gravity DN200, booster DN200 discharge feeds Bwaidha. YWC: 'UM LOLO GRAVITY TO HOSHA BOOSTER'. Keep Hosha_Booster_200. | No | Hosha_Booster_200 | 1
613 | Irbid | Ramtha | hay markez sehhi | Hosha_Booster | Hosha_Booster_200 | 557 | 589 | Fed by Hosha booster or Um Lulu PS ? | Hosha Booster (not Um Lulu PS pumps). Um Lulu Resv feeds the booster by gravity DN200, booster DN200 discharge feeds Bwaidha. YWC: 'UM LOLO GRAVITY TO HOSHA BOOSTER'. Keep Hosha_Booster_200. | No | Hosha_Booster_200 | 1
614 | Irbid | Ramtha | Hay sharqi | Hosha_Booster | Hosha_Booster_200 | 567 | 600 | Fed by Hosha booster or Um Lulu PS ? | Hosha Booster (not Um Lulu PS pumps). Um Lulu Resv feeds the booster by gravity DN200, booster DN200 discharge feeds Bwaidha. YWC: 'UM LOLO GRAVITY TO HOSHA BOOSTER'. Keep Hosha_Booster_200. | No | Hosha_Booster_200 | 1
615 | Irbid | Ramtha | Hay karama & sharia' alra'eesi | Hosha_Booster | Hosha_Booster_200 | 549 | 608 | Fed by Hosha booster or Um Lulu PS ? | Hosha Booster (not Um Lulu PS pumps). Um Lulu Resv feeds the booster by gravity DN200, booster DN200 discharge feeds Bwaidha. YWC: 'UM LOLO GRAVITY TO HOSHA BOOSTER'. Keep Hosha_Booster_200. | No | Hosha_Booster_200 | 1
623 | Mafraq | Mafraq | Um_Butaimah | Dogmseh_PS | Dogmseh_PS | 765 | 936 | Check if fed from Dogmseh_PS or Bweida_PS | Dogmseh_PS. YWC: DOGMOSEH PS. Dogmseh PS (2 pumps 50m3/h@400m/@250m, 4x25m3 tanks) is fed from Bweidha system; zone boosted by Dogmseh PS, 4 sub-zones 6h each. Keep Dogmseh_PS. | No | Dogmseh_PS | 1
624 | Mafraq | Mafraq | Hweishan | Dogmseh_PS | Dogmseh_PS | 736 | 882 | Check if fed from Dogmseh_PS or Bweida_PS | Dogmseh_PS (boosted from SP Dogmosseh - field; Dogmseh 4 km vs Bweidha PS 11 km). YWC lists BWAIDAH PS = origin of water feeding Dogmseh. Keep Dogmseh_PS; confirm booster runs every cycle. | Confirm | Dogmseh_PS | 0
625 | Mafraq | Mafraq | Ein AL Nabi | Dogmseh_PS | Dogmseh_PS | 685 | 803 | Check if fed from Dogmseh_PS or Bweida_PS | Dogmseh_PS (boosted from SP Dogmosseh - field; Dogmseh 5 km vs Bweidha PS 13 km). YWC lists BWAIDAH PS = origin of water feeding Dogmseh. Keep Dogmseh_PS; confirm booster runs every cycle. | Confirm | Dogmseh_PS | 0
626 | Mafraq | North Badia | Rahmat | Koum Ahmar ps | Koum Ahmar_PS | 694 | 729 | How many discharge lines ? split the hydraulic zone | Koum Ahmar PS has 2 pumps (50m3/h@250m, 100m3/h@100m) and 2 distribution outlets DN125 + DN100 (field notes). This zone fed by DN100 -> Koum Ahmar_PS_100. Confirm which pump feeds which line. | Confirm | Koum Ahmar_PS_100 | 0 | Yes
630 | Irbid | Irbid | Hay sad | Hosha_Booster | Hosha_Booster_200 | 564 | 599 | Fed by Hosha booster or Um Lulu PS ? | Hosha Booster (not Um Lulu PS pumps). Um Lulu Resv feeds the booster by gravity DN200, booster DN200 discharge feeds Bwaidha. YWC: 'UM LOLO GRAVITY TO HOSHA BOOSTER'. Keep Hosha_Booster_200. | No | Hosha_Booster_200 | 1
654 | Jarash | Jarash | Baleela Hay Almadares | Bowidah Ps to res | Bowidah_PS | 740 | 841 | To check P_Zone : Balela Reservoir instead of Bowidah_PS | Yes - change to Balela Resv (gravity). Bowidah PS pumps to Balela Resv; field: DN150 feeds zone (neighbours fed from Balela Resv). Change to Balela_Resv - confirm the DN150 is the Resv outlet. | Confirm | Balela_Resv | 0 | Yes
655 | Mafraq | Mafraq | Tareeq Koum Ahmar | Koum ahmar ps | Koum Ahmar_PS | 676 | 704 | How many discharge lines ? split the hydraulic zone | Fed from Koum Ahmar PS (YWC 58% TAREEQ KOUM AHMAR, Badia system, ROU Mafraq). Line diameter not in notes -> ask operator: DN100 or DN125 outlet (Koum Ahmar_PS_100 / _125). | Yes | Koum Ahmar_PS_100 | 0 | Yes
656 | Jarash | Jarash | Kabar_BAL | bowidah ps to Res_bal | Bowidah_PS | 707 | 777 | To check P_Zone : Balela Reservoir instead of Bowidah_PS | Yes - change to Balela Resv (gravity). Bowidah PS pumps to Balela Resv; field: fed from Balela Reservoir. Change to Balela_Resv (not in YWC Mafraq layer). | No | Balela_Resv | 0 | Yes