## PZ Verification
Pressure Zone Verification with Operators
Yellow cells = to be filled after checking with operators.
# | Governorate | Directorate | Zone Code | Area | Zone No. | Issue | Current PZ | Confirmed PZ (Operator) | Operator / Contact | Status | Remarks | Recommended PZ (with diameter) | Ask operator? | Basis / evidence | GIS id
Irbid Governorate – Bani Kenanah Directorate
1 | Irbid | Bani Kenanah | Irb_Ban_Kuf_6 | Kuf | 6 | PZ uncertain – verify with operators (from attached list) | Harima_PS_200 |  |  | Operator needed |  | Harima_PS_200 + Bait_Ras_Res_400 (mixed) | Yes | Notes: DN200 from Harima PS (465 m, 3 km) with DN150 branches, plus DN200 branches off the DN400 Bait Ras line. Ask which part each line feeds -> split candidate. | 470
2 | Irbid | Bani Kenanah | Irb_Ban_Sam_7 | Sam | 7 | PZ uncertain – verify with operators (from attached list) | Harima_PS_200 |  |  | Operator needed |  | Harima_PS_200 (main) + Bait_Ras_Res_400 + Malka_PS (north) - mixed | Yes | Notes: DN200 from Harima PS with DN150 branch to the DN400 (Bait Ras); from the north a pipe from Malka PS (451 m) brings mixed water - Malka pipe size not in notes. Ask which areas each source serves. | 471
3 | Irbid | Bani Kenanah | Irb_Ban_HBR_9 | HBR | 9 | PZ uncertain – verify with operators (from attached list) | Harima_PS_200 |  |  | Answered - confirm |  | Harima_PS_200 | Confirm | Notes: two DN150 lines from the DN200 = Harima PS discharge (same DN200 as Kufr Jayez / Sama Al-Rousan). Bait Ras is named in the Source field but not in the notes. | 473
Irbid Governorate – Irbid Qasabah Directorate
4 | Irbid | Irbid Qasabah | Irb_Irb_Ass_20 | Ass | 20 | PZ uncertain – verify with operators | Assara_PS |  |  | Answered - ask diameter |  | Assara_PS (diameter not in notes) | Confirm | Notes: area is pressurised by Assara PS (293 m). Zabda Resv only refills the Assara reservoir after Foara and Hour are supplied = water origin, not the pressure zone. Ask operator the discharge diameter. | 38
5 | Irbid | Irbid Qasabah | Irb_Irb_Foa_21 | Foa | 21 | PZ uncertain – verify with operators | Foara_PS |  |  | Confirm with operator |  | Zabda_Resv (scheduled Thu-Fri) / Foara_PS (weekdays) - diameter not in notes | Confirm | Notes: Foara well on weekdays, Zabda on Thu-Fri. The zone schedule (Thu 3PM-Fri 11PM) is the Zabda period, so the scheduled supply is from Zabda Resv. Time-based dual source - no spatial split. Ask the feeding diameter. | 39
6 | Irbid | Irbid Qasabah | Irb_Irb_Hou_22 | Hou | 22 | PZ uncertain – verify with operators | Foara_PS |  |  | Answered - confirm name |  | Zabda_Resv (main); Foara_PS only exceptionally - diameter not in notes | Confirm | Notes: normally supplied from Zabda Thu-Fri, only exceptionally from Foara well; split into ~6 h sub-zones. Change P_Zone from Foara_PS to Zabda. Ask the feeding diameter and whether Zabda supply is gravity or via Zabda_PS. | 40
7 | Irbid | Irbid Qasabah | Irb_Irb_Sam_39 | Sam | 39 | PZ uncertain – verify with operators | Mandah_PS1_200 |  |  | Answered |  | Mandah_PS1_200 | No | Notes: Mandah wells 1+3 via DN200 to near Al-Tayybeh PS, then 2xDN100 + DN150 with one rotation per line. Al-Tayybeh well is not feeding (the DN200 only passes near it). GIS network not updated. | 57
8 | Irbid | Irbid Qasabah | Irb_Irb_Mek_40 | Mek | 40 | PZ uncertain – verify with operators | Mandah_PS1_200 |  |  | Answered |  | Mandah_PS1_200 | No | Notes: Mandah wells 1+3 via DN200 to near Al-Tayybeh PS, then DN100. Al-Tayybeh well is not feeding. Mandah PS1 at 307 m, zone 143-242 m. GIS network not updated. | 58
Mafraq Governorate – Mafraq Qasabah Directorate
9 | Mafraq | Mafraq Qasabah | Maf_Maf_Hay_110 | Hay | 110 | PZ uncertain – verify with operators | Zaatary_PS_100_Univ | Zaatary_PS_100_Univ | Operator call (Oct 2026) | Confirmed (operator) |  | Zaatary_PS_100_Univ | No | Operator call (Oct 2026): fed from Zaatari PS, 4in (DN100) line from the University pump - not Zubaidiyeh PS. Older YWC layer still lists Zubaidiyeh PS (200 m away). | 417
10 | Mafraq | Mafraq Qasabah | Maf_Maf_Tar_111 | Tar | 111 | PZ uncertain – verify with operators | BAEJ_PS_100 |  |  | Confirm with operator |  | BAEJ 3_PS_100 | Confirm | Operator call: 'Baej PS, 4in steel line' (DN100), not Zubaidiyeh. Baej 3 is the nearer Baej station (2.3 km vs 3.1 km for Baej 2) and its outlet is 4in steel, while Baej 2 uses a 6in line -> most likely Baej 3. GIS now: BAEJ_PS_100. | 418
Total zones: |  |  | 10

## Split Distribution Zones
Distribution Zones with Two Supply Sources – Split Check
Yellow cells = to be filled after checking with operators.
# | Governorate | Directorate | Zone Code | Area | Zone No. | Issue | Supply Source 1 | Supply Source 2 | Split Possible? (Y/N) | New Polygon Codes | Status | Remarks | New polygon P_Zones (with diameter) | GIS id | GIS P_Zone (now)
Ajloun Governorate – Ajloun Qasabah Directorate
1 | Ajloun | Ajloun Qasabah | Ajl_Ajl_Ain_20 | Ain | 20 | Two supply sources – split polygon by source | Ajloun Reservoir (gravity, 956 m) - main | Ain Janna spring PS (840 m) - small amount | N |  | Not split | Ain Janna adds a small volume into the same network. Only ~2-5% of the zone is above the reservoir gravity limit (916-936 m), as scattered high points - not a separate area. Keep one zone. Diameter not in notes. |  | 149 | Ajloun_Res_Ain_Janna_PS
Irbid Governorate – Bani Kenanah Directorate
2 | Irbid | Bani Kenanah | Irb_Ban_Kit_40 | Kit | 40 | Two supply sources – split polygon by source | No'aymeh PS1 - Noima_PS1_150 | No'aymeh PS4 - Noima_PS4_100 | Y (boundary needed) | Irb_Ban_Kit_40_A (PS1) / Irb_Ban_Kit_40_B (PS4) - not drawn | Operator needed | Two separate lines (DN150 from PS1, DN100 from PS4) so a spatial split is possible, but no pipe network for this area to draw the boundary. Both PS are pumped (720 m / 704 m). Ask operator to mark the DN150/DN100 service areas. | Noima_PS1_150 / Noima_PS4_100 | 274 | Noima_PS1_PS4_150
Irbid Governorate – Irbid Qasabah Directorate
3 | Irbid | Irbid Qasabah | Irb_Irb_Al-_33 | Al- | 33 | Two supply sources – split polygon by source | Rahoub PS (24h/7, inside zone, 423 m) | Bushra PS / Resv 500 m3 (3 days per week, 531 m) | N (time-based) |  | Confirm with operator | Notes: zone divided into 4 sub-zones, fed from Bushra 3 days and Rahoub 24h/7 - supply overlaps in time over the same network, no source boundary. Ask if any sub-zone is fed by Bushra only, and the line diameters. |  | 51 | Rahoub_PS
Mafraq Governorate – Mafraq Qasabah Directorate
4 | Mafraq | Mafraq Qasabah | Maf_Maf_Tha_8 | Tha | 8 | Two supply sources – split polygon by source | Za'tary PS | Thaghret Al Job local well (summer) | N (seasonal) |  | Not split | YWC: "Zaatary PS and Thaghret Job Well (Summer)" - the well is a seasonal supplement into the same network. The 3 sub-zones are supply rotations, not source areas. Diameter not in notes. |  | 315 | Thagret_Al_Job+Zaatary_PS
5 | Mafraq | Mafraq Qasabah | Maf_Maf_Hay_140 | Hay | 140 | Two supply sources – split polygon by source | Balaama Resv (gravity, 10in) -> Hay Aggad | Znayah PS (DN200) -> Balaama Hay Shamali | Y | Maf_Maf_Hay_140_A / Maf_Maf_Hay_140_B | Split done - confirm | Cut along YWC zones 96/97 (63% / 37% on Distribution_Zone14_9_2026). Operator confirmed mixed supply. CHECK: 42% of Hay Aggad is above 716 m while the Balaama tank is at ~736 m - sources may be swapped between A and B. | Balaama_Resv_250_G / Znayah_PS_200 | 447 | Znayah_PS_200
Mafraq Governorate – Northern Badia Directorate
6 | Mafraq | Northern Badia | Maf_Nor_Man_40 | Man | 40 | Two supply sources – split polygon by source | Dafyaneh / Mukefteh PS (DN200) | Sabha PS (DN150) | Y | Maf_Nor_Man_40_A / Maf_Nor_Man_40_B | Split done | Cut along YWC zones 26/30 (59% / 41% on Distribution_Zone14_9_2026). The Sabha part is in YWC zone 30 (SABHA, Sabha PS), which also covers GIS zone 108 Sabha (Sabha_PS_150). | Dafyaneh ps , Mukefteh PS_200 / Sabha_PS_150 | 109 | Dafyaneh ps , Mukefteh PS_200
7 | Mafraq | Northern Badia | Maf_Nor_Daf_41 | Daf | 41 | Two supply sources – split polygon by source | Dafyaneh PS (inside zone, DN200 + DN150) | Mukefteh PS (via connecting DN200) | N |  | Not split | Dafyaneh PS and Mukefteh PS are connected by the same DN200 and share it in time. YWC treats the area as one zone (MKAIFTEH PS). Keep one zone: Dafyaneh ps , Mukefteh PS_200. |  | 110 | Dafyaneh ps , Mukefteh PS_200
8 | Mafraq | Northern Badia | Maf_Nor_Hay_42 | Hay | 42 | Two supply sources – split polygon by source | Dafyaneh PS (DN150 line) | - | N |  | Not split | Notes: fed only by DN125/63 branches from one DN150 line - single feed. P_Zone: Dafyaneh ps , Mukefteh PS_150. |  | 111 | Dafyaneh ps , Mukefteh PS_150
9 | Mafraq | Northern Badia | Maf_Nor_Khs_43 | Khs | 43 | Two supply sources – split polygon by source | Dafyaneh PS (DN200) | Mukefteh PS (same DN200) | N (time-based) |  | Not split | Notes: fed from the same DN200 that connects both PS - half the time from Dafyaneh PS, half from Mukefteh PS. Same pipe, so no spatial split. P_Zone: Dafyaneh ps , Mukefteh PS_200. |  | 112 | Dafyaneh ps , Mukefteh PS_200
10 | Mafraq | Northern Badia | Maf_Nor_Hay_44 | Hay | 44 | Two supply sources – split polygon by source | Dafyaneh PS (DN125 from DN200) | - | N |  | Not split | Notes: single DN125 from the DN200. Very small zone (0.15 km2). P_Zone: Dafyaneh ps , Mukefteh PS_200. |  | 113 | Dafyaneh ps , Mukefteh PS_200
Total zones: |  |  | 10