## PZ Verification
Pressure Zone Verification with Operators
Yellow cells = to be filled after checking with operators.
# | Governorate | Directorate | Zone Code | Area | Zone No. | Issue | Current PZ | Confirmed PZ (Operator) | Operator / Contact | Status | Remarks | Distribution Zone Name (My_Zone_Name) | Region (My_Region) | Master plan zones (ZIM) | Recommended PZ (with diameter) | Ask operator? | Evidence (field notes / YWC / operator / Master Plan) | GIS id
Irbid Governorate – Al-Koura Directorate
1 | Irbid | Al-Koura | Irb_Kou_Jud_20 | Jud | 20 | PZ uncertain – verify with operators (from attached list) | Judyta_Booster_150 |  |  | Answered |  | Judyta | Irbid_Koura | Judaita-97% | Judyta_Booster_150 | No | ZIM: Judaita 97%. MP sheet I-JD: JUDAITA (300-710 m) is fed from Jditta Booster by DN150; the booster is filled by Jditta PS (325 m) DN300 rising main. Field notes agree (area fed by DN150 from the booster; a few customers near the PS on DN150 tapped on the DN300). P_Zone Judyta_PS -> Judyta_Booster_150. | 645
Irbid Governorate – Bani Kenanah Directorate
2 | Irbid | Bani Kenanah | Irb_Ban_Kuf_6 | Kuf | 6 | PZ uncertain – verify with operators (from attached list) | Harima_PS_200 |  |  | Answered - confirm |  | Kufer jayez | Irbid-Bani Kinana | JAYZ-87%/SAM-6% | Bait_Ras_Res_200_G + Harima_PS_200 (mixed) | Confirm | ZIM: JAYZ 87%. MP sheet I-BAT: JAYZ fed by gravity from Bait Ras Res (4000 m3, 605 m) DN400 -> DN200 branch; Harima Res PS (465 m) pumped DN200 joins the same line. Field notes agree (Harima DN200 + DN200 off DN400). One MP zone - no split. | 470
3 | Irbid | Bani Kenanah | Irb_Ban_Sam_7 | Sam | 7 | PZ uncertain – verify with operators (from attached list) | Harima_PS_200 |  |  | Operator needed |  | Sama Alrosan | Irbid-Bani Kinana | SAM-96% | Malka_PS_300 (MP) - field adds Harima_PS_200 + Bait Ras DN400 | Yes | ZIM: SAM 96%. MP sheet I-KU6: SAM fed only from Malka Res PS (442 m) pumped DN300 main -> DN150 branch. Field notes: Harima DN200 + DN150 to Bait Ras DN400 + Malka from north (mixed). Ask operator which is the main source today. | 471
4 | Irbid | Bani Kenanah | Irb_Ban_HBR_9 | HBR | 9 | PZ uncertain – verify with operators (from attached list) | Harima_PS_200 |  |  | Operator needed |  | HBRAS | Irbid-Bani Kinana | HBRS-98% | Bait_Ras_Res_100_G (MP) / Harima_PS_200 (field) | Yes | ZIM: HBRS 98%. MP sheet I-BAT: HBRS fed by gravity from Bait Ras Res DN400 -> DN100 branch. Field notes: two DN150 from a DN200 (Harima). Sources disagree - ask operator. | 473
Irbid Governorate – Irbid Qasabah Directorate
5 | Irbid | Irbid Qasabah | Irb_Irb_Ass_20 | Ass | 20 | PZ uncertain – verify with operators | Assara_PS |  |  | Answered - confirm |  | Assara | North-Irbid | Z_GR_10.1.E-100% | Assara_PS_100 | Confirm | ZIM: GR 10.1.E 100%. MP sheet I-ZAB: GR 10.1.E (180-370 m) on DN100 after PRV at the end of the Zabda gravity cascade. Field: area pressurised by Assara PS, Assara Res refilled from Zabda. Diameter DN100 from MP; confirm Assara PS discharge size. | 38
6 | Irbid | Irbid Qasabah | Irb_Irb_Foa_21 | Foa | 21 | PZ uncertain – verify with operators | Foara_PS |  |  | Answered - split candidate |  | Foara | North-Irbid | Z_GR_10.1.C-67%/Z_GR_10.1.D-24%/Z_GR_10.1.E-6% | Zabda_Res_150_G (Thu-Fri) / Foara_PS (weekdays) - split C/D | Confirm | ZIM: GR 10.1.C 67% / GR 10.1.D 24%. MP sheet I-ZAB: Zabda Res (630 m) gravity cascade - GR 10.1.C on DN150, GR 10.1.D on DN125 (PRVs). Field: Foara well weekdays, Zabda Thu-Fri (= zone schedule). Split possible along MP C/D boundary. | 39
7 | Irbid | Irbid Qasabah | Irb_Irb_Hou_22 | Hou | 22 | PZ uncertain – verify with operators | Zabda_Res_150_G |  |  | Answered |  | Hour | North-Irbid | Z_GR_10.1.C-99% | Zabda_Res_150_G | No | ZIM: GR 10.1.C 99%. MP sheet I-ZAB: GR 10.1.C fed by gravity DN150 (PRV) from Zabda Res. Field: normally Zabda Thu-Fri, Foara well only exceptionally. Change P_Zone Foara_PS -> Zabda_Res_150_G. | 40
8 | Irbid | Irbid Qasabah | Irb_Irb_Sam_39 | Sam | 39 | PZ uncertain – verify with operators | Mandah_PS1_200 |  |  | Answered |  | Samaa | Taybeh | Sum3-29%/Sum2-26%/Sum1-16% | Mandah_PS1_200 | No | ZIM: Sum3 29% / Sum2 26% / Sum1 16%. MP sheet I-MAN: Mandah PS1 (500 m3, 305 m) outlets DN200 + DN150; SUM1/SUM3 on DN100 off DN150, SUM2 off DN150 and DN200 (DN125). Field: DN200 -> 2xDN100 + DN150. Al-Tayybeh not feeding. | 57
9 | Irbid | Irbid Qasabah | Irb_Irb_Mek_40 | Mek | 40 | PZ uncertain – verify with operators | Mandah_PS1_200 |  |  | Answered |  | Mekheraba | Taybeh | NO MATCH FOUND | Mandah_PS1_200 | No | MP sheet I-MAN: MAK (Makhraba, 235-423 m) fed from Mandah PS1 DN200 main -> DN100 -> DN150. ZIM had no match >=5% (MP zone MAK not in the other-company layer). Field notes agree (DN200 from Mandah). | 58
Irbid Governorate – Ramtha Directorate
10 | Irbid | Ramtha | Irb_Ram_was_5 | was | 5 | PZ uncertain – verify with operators (from attached list) | Zatari' PS and abu albasaal PS_300 |  |  | Answered - confirm 2nd source |  | wast albalad | Ramtha | RA3-99% | Zatari' PS_300 (main) + Al hodoud PS_200 (field) | Confirm | ZIM: RA3 99%. MP sheet I-ZAT: RA3 fed from the Za'tary DN300 main (DN150 branch); MP shows no second source. Field notes add a DN200 from Al Hodoud PS. Abu Al-Basal (in current GIS P_Zone) is NOT a source - fix name. | 595
11 | Irbid | Ramtha | Irb_Ram_Al _6 | Al | 6 | PZ uncertain – verify with operators (from attached list) | Zatari' PS and abu albasaal PS_300 |  |  | Answered - confirm 2nd source | Code contains a space – check spelling in GIS | Al tatoieer alhadarie | Ramtha | RA8-42%/RA2-32%/RA5-24% | Zatari' PS_400 (main) + Al hodoud PS (field) | Confirm | ZIM: RA8 42% / RA2 32% / RA5 24%. MP sheet I-ZAT: all three on the Za'tary DN400 main (DN200 / DN180+150 / DN200 branches). Field: Al Hodoud PS also feeds the high area. Abu Al-Basal not a source. Code has a space - suggest Irb_Ram_Alt_6. | 596
12 | Irbid | Ramtha | Irb_Ram_soo_7 | soo | 7 | PZ uncertain – verify with operators (from attached list) | Zatari' PS and abu albasaal PS_300 |  |  | Answered - confirm |  | sooq | Ramtha | RA5-55%/RA4-30%/RA1-11% | Zatari' PS_400 + Al hodoud PS (alternating by valves) | Confirm | ZIM: RA5 55% / RA4 30% / RA1 11%. MP sheet I-ZAT: RA5/RA4/RA1 on the Za'tary DN400 main (DN200/DN100 branches). Field: valve cluster alternates north/south between Al Hodoud and Za'tary. Abu Al-Basal not a source. | 597
13 | Irbid | Ramtha | Irb_Ram_Hay_8 | Hay | 8 | PZ uncertain – verify with operators (from attached list) | Zatari' PS and abu albasaal PS_300 |  |  | Operator needed |  | Hay sharqi | Ramtha | RA6-22% | Zatari' PS_400 + Al hodoud PS (field) | Yes | ZIM: RA6 22% only (weak match). MP sheet I-ZAT: RA6 on Za'tary DN400 main (DN150 branch). Field: two sources Za'tary + Al Hodoud. Abu Al-Basal not a source. Ask operator. | 598
14 | Irbid | Ramtha | Irb_Ram_Al _9 | Al | 9 | PZ uncertain – verify with operators (from attached list) | Zatari' PS and abu albasaal PS_300 |  |  | Operator needed | Code contains a space – check spelling in GIS | Al dhadah | Ramtha | RA14-82% | Al hodoud PS_200 (MP) / Zatari' + Abu Al-Basal (field) | Yes | ZIM: RA14 82%. MP sheet I-JH: RA14 fed from Jaber Al-Hodoud PS (519 m) DN200 main (DN150 + DN100). Field notes say Za'tary branch + Abu Al-Basal DN200->DN300. Sources disagree - ask operator. Code has a space - suggest Irb_Ram_Ald_9. | 599
15 | Irbid | Ramtha | Irb_Ram_dab_10 | dab | 10 | PZ uncertain – verify with operators (from attached list) | Zatari' PS and abu albasaal PS_300 |  |  | Answered - split candidate |  | dabet Nemer | Ramtha | RA12-71%/RA7-22%/RA19-5% | Abu Al-basal_PS_300 (south) + Zatari' PS_400 (north) - split | No | ZIM: RA12 71% / RA7 22%. MP sheets I-BAS / I-ZAT: RA12 fed from Abu Al-Basal PS (515 m) DN300 main; RA7 from the Za'tary DN400 main (DN150). Matches field notes exactly (south DN300 Abu Al-Basal, north DN300 Za'tary). Split along MP RA12/RA7 boundary (needs Ramtha zones layer). | 600
Mafraq Governorate – Mafraq Qasabah Directorate
16 | Mafraq | Mafraq Qasabah | Maf_Maf_Hay_110 | Hay | 110 | PZ uncertain – verify with operators | Zaatary_PS_100_Univ | Zaatary_PS_100_Univ | Operator call (Oct 2026) | Conflict - reconfirm |  | Hay Nada Zbadi | Mefraq | ZU6-93%/ZU7-6% | Zaatary_PS_100_Univ (operator) - MP shows Al Zubaideyeh_PS_100 | Confirm | Operator call (Oct 2026): Zaatari PS, 4in from the University pump. But ZIM: ZU6 93% and MP sheet M-ZU: ZU6 fed from Zubaidyeh PS (680 m) DN100; field note and YWC also say Zubaidiyeh. Kept operator answer - please reconfirm. | 417
17 | Mafraq | Mafraq Qasabah | Maf_Maf_Tar_111 | Tar | 111 | PZ uncertain – verify with operators | BAEJ_PS_100 |  |  | Conflict - reconfirm |  | Tareeq Al Nahdah | Mefraq | ZU5-84% | Al Zubaideyeh_PS_150 | Confirm | ZIM: ZU5 84%. MP sheet M-ZU: ZU5 fed from Zubaidyeh PS DN150. Field note ('from 150 mm from PS'), YWC (ZUBAIDIYYEH PS) agree. Only the operator call said 'Baej PS 4in'. Recommend Al Zubaideyeh_PS_150 - reconfirm with operator. MP also shows Zubaidyeh PS feeds Umm Serb PS by DN150. | 418
Total zones: |  |  | 17

## Split Distribution Zones
Distribution Zones with Two Supply Sources – Split Check
Yellow cells = to be filled after checking with operators.
# | Governorate | Directorate | Zone Code | Area | Zone No. | Issue | Supply Source 1 | Supply Source 2 | Split Possible? (Y/N) | New Polygon Codes | Status | Remarks | Distribution Zone Name (My_Zone_Name) | Region (My_Region) | Master plan zones (ZIM) | New polygon P_Zones (with diameter) | GIS id | GIS P_Zone (now)
Ajloun Governorate – Ajloun Qasabah Directorate
1 | Ajloun | Ajloun Qasabah | Ajl_Ajl_Ain_20 | Ain | 20 | Two supply sources – split polygon by source | Ajloun Res (953 m) gravity DN150->DN100 -> AJ2 part (21%) | Ain Jana PS (843 m) pumped DN150->DN100 -> AIJ4+AIJ5 part (60%) | Y | Ajl_Ajl_Ain_20_A (AJ2) / Ajl_Ajl_Ain_20_B (AIJ4+AIJ5) | Split - needs Ajloun_Zones layer | ZIM: AIJ5 41% / AJ2 21% / AIJ4 19%. MP sheet A-KU shows two pressure zones: AJ2 by gravity from Ajloun Res, AIJ4/AIJ5 pumped from Ain Jana PS (the PS tank is filled from Ajloun Res - so water is mainly Ajloun's, as the field note says). Cut along MP zone boundary. | Ain Janna | Ajloun | AIJ5-41%/AJ2-21%/AIJ4-19% | Ajloun_Res_150_G / Ain_Janna_PS_150 | 149 | Ajloun_Res_Ain_Janna_PS_150
Irbid Governorate – Bani Kenanah Directorate
2 | Irbid | Bani Kenanah | Irb_Ban_Kit_40 | Kit | 40 | Two supply sources – split polygon by source | No'ayma PS1 (723 m): KE-1 DN150 + SH/NOM DN100 (90%) | No'ayma PS4 (709 m): NOM-1 DN100 (8%) | Y | Irb_Ban_Kit_40_A (PS1) / Irb_Ban_Kit_40_B (PS4) | Split - needs Noayymeh zones layer | ZIM: KE_1 53% / SH/NOM 37% / NOM_1 8%. MP sheets I-NO1 / I-NO4: KE-1 and SH/NOM from No'ayma PS1, NOM-1 from No'ayma PS4. Matches field note (150 from PS1, 100 from PS4). Cut PS1 part = KE_1+SH/NOM, PS4 part = NOM_1. | Kitem Aljanoobi | Irbid-Obeid | KE_1-53%/SH/NOM-37%/NOM_1-8% | Noima_PS1_150 / Noima_PS4_100 | 274 | Noima_PS1_PS4_150
Irbid Governorate – Irbid Qasabah Directorate
3 | Irbid | Irbid Qasabah | Irb_Irb_Al-_33 | Al- | 33 | Two supply sources – split polygon by source | Zabda Res gravity DN400 -> DN150 -> GR 9.3.C part (67%) | Rahoub PS (24h/7) -> remaining 33% | Y | Irb_Irb_Al-_33_A (GR 9.3.C) / Irb_Irb_Al-_33_B (rest) | Split - needs Irbid zones layer (confirm) | ZIM: GR 9.3.C 67%, rest not in any MP Irbid zone. MP sheet I-ZAB: GR 9.3.C on DN150 off the Zabda DN400 gravity main. Field: Bushra 3 days + Rahoub 24h/7 over 4 sub-zones. Confirm with operator that the GR 9.3.C part = the Bushra/Zabda side. | Al-Maghayer_Zumla | East-Irbid | Z_GR_9.3.C-67% | Zabda_Res_150_G / Rahoub_PS | 51 | Rahoub_PS
Mafraq Governorate – Mafraq Qasabah Directorate
4 | Mafraq | Mafraq Qasabah | Maf_Maf_Tha_8 | Tha | 8 | Two supply sources – split polygon by source | Za'atary PS DN400 -> DN300 | Thaghrat Job PS (667 m) DN100 | N |  | Not split | ZIM: ZA_T1 79%. MP sheet M-ZAAT: AZ_T1 is ONE zone fed by both sources into the same network - no MP boundary to split on. | Thagret_Al_Job | Al-Mafraq | ZA_T1-79% | Thagret_Al_Job_100+Zaatary_PS_300 | 315 | Thagret_Al_Job_100+Zaatary_PS_300
5 | Mafraq | Mafraq Qasabah | Maf_Maf_Hay_140 | Hay | 140 | Two supply sources – split polygon by source | Balaama Res (735 m) gravity DN200 -> DN150 -> Hay Aggad (BLG4) | Znayya PS (620 m) pumped DN200 -> Balaama Hay Shamali (ZN30) | Y | Maf_Maf_Hay_140_A / Maf_Maf_Hay_140_B | Split done - confirmed by MP | ZIM: BLG4 59% / ZN30 36%. MP sheet M-ZN confirms A = gravity from Balaama Res (BLG-4, 660-715 m), B = Znayya PS DN200 (ZN-30). Earlier elevation doubt resolved - no swap needed. | Hay AGGAD and Balaama Hay shamali | Mefraq | BLG4-59%/ZN30-36% | Balaama_Resv_250_G / Znayah_PS_200 | 447 | Znayah_PS_200
Mafraq Governorate – Northern Badia Directorate
6 | Mafraq | Northern Badia | Maf_Nor_Man_40 | Man | 40 | Two supply sources – split polygon by source | Mukaifteh / Dafyaneh PS DN200 (MK3) | Sabha PS (833 m) DN150 (SA1) | Y | Maf_Nor_Man_40_A / Maf_Nor_Man_40_B | Split done - confirmed by MP | ZIM: MK3 59% / SA1 41%. MP sheets M-MUK and Sabha: MK3 fed from Mukaifteh DN200 main + Al-Dafyaneh PS; SA1 fed from Sabha PS DN150. | Manshiet algoblan | Badia | MK3-59%/SA1-41% | Dafyaneh ps , Mukefteh PS_200 / Sabha_PS_150 | 109 | Dafyaneh ps , Mukefteh PS_200
7 | Mafraq | Northern Badia | Maf_Nor_Daf_41 | Daf | 41 | Two supply sources – split polygon by source | Mukaifteh PS (922 m) DN200 main -> DN150/DN100 | Al-Dafyaneh PS (898 m) DN200 -> DN100 (tank filled from Mukaifteh main) | N |  | Not split | ZIM: MK3 100%. MP sheet M-MUK: MK3 is one zone fed from both into the same network - no boundary. | Dafyaneh | Badia | MK3-100% | Dafyaneh ps , Mukefteh PS_200 | 110 | Dafyaneh ps , Mukefteh PS_200
8 | Mafraq | Northern Badia | Maf_Nor_Hay_42 | Hay | 42 | Two supply sources – split polygon by source | Mukaifteh / Dafyaneh (MK3) DN150 line | - | N |  | Not split | ZIM: MK3 100% - same single MP zone as Dafyaneh. Field: single DN150 feed. | Hay Alhelo | Badia | MK3-100% | Dafyaneh ps , Mukefteh PS_150 | 111 | Dafyaneh ps , Mukefteh PS_150
9 | Mafraq | Northern Badia | Maf_Nor_Khs_43 | Khs | 43 | Two supply sources – split polygon by source | Mukaifteh PS DN200 main (MK2) | Dafyaneh PS (same DN200, time-shared) | N (time-based) |  | Not split | ZIM: MK2 89% / MK1 11% - both MK2 and MK1 fed from the same Mukaifteh DN200 main (one source). Field: same DN200 shared in time. | Khshaa Slaiteyeen | Badia | MK2-89%/MK1-11% | Dafyaneh ps , Mukefteh PS_200 | 112 | Dafyaneh ps , Mukefteh PS_200
10 | Mafraq | Northern Badia | Maf_Nor_Hay_44 | Hay | 44 | Two supply sources – split polygon by source | Mukaifteh DN200 main (MK2) -> DN125 | - | N |  | Not split | ZIM: MK2 92% / MK1 8% - same source (Mukaifteh). Single DN125 feed, 0.15 km2. | Hay algomaad | Badia | MK2-92%/MK1-8% | Dafyaneh ps , Mukefteh PS_200 | 113 | Dafyaneh ps , Mukefteh PS_200
Total zones: |  |  | 10

## Diameter fill (Master Plan)
Diameters from Master Plan Vol II Elevation Schematics + Zone_Intersection_Matching for zones that had no diameter. Applied = Yes -> written into P_Zone in the shapefile; "No - confirm first" -> suggestion kept in field PZ_MP.
id | code | Sub_zone | My_Zone_Name | ROU | P_Zone_before | P_Zone_now | Master_plan_PZ | Diameter | Confidence | MP_zone_codes | MP_sheet | Basis | Note | Applied
19 | Irb_Irb_Eas_1 | East_Kufr_Asad | East_Kufr_Asad | Irbid | Kufr_Asad_Wells_1_7_PS | Kufr_Asad_Wells_1_7_PS_150 | Kufr_Asad_Wells_1_7_PS_150 | 150 | High | KUA1 59% / KUA2 30% | I-KU1 (p10) | Master plan schematic | Kufr Asad PS (260 m) pumped DN150 main; zone on DN100/125 branches | Yes
20 | Irb_Irb_Wes_2 | West_Kufr_Asad | West_Kufr_Asad | Irbid | NULLKufr_Asad_Wells_1_7_PS | Kufr_Asad_Wells_1_7_PS_150 | Kufr_Asad_Wells_1_7_PS_150 | 150 | High | KUA2 47% / KUA4 24% | I-KU1 (p10) | Master plan schematic | Kufr Asad PS pumped DN150 main, DN100/125 branches. GIS name had "NULL" prefix - cleaned | Yes
21 | Irb_Irb_Sai_3 | Saidour | Saidour | Irbid | Kufr_Asad_Wells_1_7_PS | Kufr_Asad_Wells_1_7_PS_150 | Kufr_Asad_Wells_1_7_PS_150 | 150 | High | SY 41% / KUA4 37% | I-KU1 (p10) | Master plan schematic | Kufr Asad PS pumped DN150 main, DN100 branches | Yes
22 | Irb_Irb_Kha_4 | Kharaj | Kharaj | Irbid | Waslat_Wadi_Arab_Connection | Waslat_Wadi_Arab_Connection | Kufr_Asad_Wells_1_7_PS_150 | 150 | Confirm | KUA3 65% / KAR 34% | I-KU1 (p10) | Master plan schematic | MP: 65% of zone is KUA3 on the Kufr Asad DN150 main; GIS P_Zone says Waslat_Wadi_Arab_Connection - confirm source | No - confirm first
28 | Irb_Irb_Dou_10 | Dougara | Dougara | Irbid | Dougara_Wells | Dougara_Wells_100 | Dougara_Wells_100 | 100 | High | DU 96% | I-WA (p28) | Master plan schematic | Dugarah well PS (25 m3, 330 m) pumps DN100; zone also connected to the Wadi Arab DN150 main | Yes
29 | Irb_Irb_Kuf_11 | Kufr-Rahtah | Kufr-Rahtah | Irbid | Waslat_Wadi_Arab_Connection | Waslat_Wadi_Arab_Connection_150 | Waslat_Wadi_Arab_Connection_150 | 150 | High | KUR 85% | I-WA (p28) | Master plan schematic | Wadi Arab PS3 DN800 -> DN150 main; KUR on DN100 branch | Yes
30 | Irb_Irb_Zah_12 | Zahar_West | Zahar_West | Irbid | Waslat_Wadi_Arab_Connection | Waslat_Wadi_Arab_Connection_150 | Waslat_Wadi_Arab_Connection_150 | 150 | High | ZA 98% | I-WA (p28) | Master plan schematic | Wadi Arab DN150 main; ZA on DN100+DN150 branches | Yes
31 | Irb_Irb_Juj_13 | Jujine | Jujine | Irbid | Waslat_Wadi_Arab_Connection | Waslat_Wadi_Arab_Connection_150 | Waslat_Wadi_Arab_Connection_150 | 150 | High | JIJ 74% / SOM 24% | I-WA (p28) | Master plan schematic | Wadi Arab DN150 main; JIJ on 2xDN100 branches (SOM on DN250) | Yes
32 | Irb_Irb_Zah_14 | Zahar_North | Zahar_North | Irbid | Waslat_Wadi_Arab_Connection | Waslat_Wadi_Arab_Connection_150 | Waslat_Wadi_Arab_Connection_150 | 150 | High | ZA 94% | I-WA (p28) | Master plan schematic | Wadi Arab DN150 main; ZA on DN100+DN150 branches | Yes
33 | Irb_Irb_Zah_15 | Zahar_South | Zahar_South | Irbid | Waslat_Wadi_Arab_Connection | Waslat_Wadi_Arab_Connection_150 | Waslat_Wadi_Arab_Connection_150 | 150 | High | ZA 100% | I-WA (p28) | Master plan schematic | Wadi Arab DN150 main; ZA on DN100+DN150 branches | Yes
34 | Irb_Irb_Jam_16 | Jamha_Center | Jamha_Center | Irbid | Waslat_Wadi_Arab_Connection | Waslat_Wadi_Arab_Connection_200 | Waslat_Wadi_Arab_Connection_200 | 200 | High | JM 96% | I-WA (p28) | Master plan schematic | Wadi Arab DN200 main; JM on DN150 branch | Yes
35 | Irb_Irb_Jam_17 | Jamha_low_zone | Jamha_low_zone | Irbid | Waslat_Wadi_Arab_Connection | Waslat_Wadi_Arab_Connection | Waslat_Wadi_Arab_Connection_200 | 200 | Confirm | YU4 44% / JM 38% / YU3 17% | I-WA (p28), I-JU (p22) | Master plan schematic | Mixed in MP: JM part on Wadi Arab DN200; YU3/YU4 part from Juhfiyya PS (DN200 -> DN150). Split candidate | No - confirm first
37 | Irb_Irb_Jam_19 | Jamha_Upper_zone | Jamha_Upper_zone | Irbid | Waslat_Wadi_Arab_Connection | Waslat_Wadi_Arab_Connection | Juhfiyya_Wells_PS_200 | 200 | Confirm | YU4 94% | I-JU (p22) | Master plan schematic | MP: YU4 fed from Juhfiyya PS (631 m) DN200 -> DN150 branch, not Wadi Arab. Field notes say Wadi Arab head after valve closing - confirm | No - confirm first
38 | Irb_Irb_Ass_20 | Assara | Assara | Irbid | Assara_PS | Assara_PS | Assara_PS_100 | 100 | Confirm | GR 10.1.E 100% | I-ZAB (p7) | Master plan schematic | MP: GR 10.1.E fed by DN100 (after PRV) on the Zabda gravity cascade; field: pressurised by Assara PS. Confirm Assara PS discharge size | No - confirm first
39 | Irb_Irb_Foa_21 | Foara | Foara | Irbid | Foara_PS | Foara_PS | Zabda_Res_150_G | 150 | Confirm | GR 10.1.C 67% / GR 10.1.D 24% | I-ZAB (p7) | Master plan schematic | MP: Zabda Res (630 m) gravity, GR 10.1.C on DN150, GR 10.1.D on DN125 (PRVs). Thu-Fri from Zabda, weekdays Foara well. Split candidate C/D | No - confirm first
40 | Irb_Irb_Hou_22 | Hour | Hour | Irbid | Foara_PS | Zabda_Res_150_G | Zabda_Res_150_G | 150 | High | GR 10.1.C 99% | I-ZAB (p7) | Master plan schematic | MP: GR 10.1.C on DN150 from Zabda gravity cascade; field: normally Zabda Thu-Fri | Yes
41 | Irb_Irb_Tog_23 | Togbuol | Togbuol | Irbid | Aydun-tagarb | Aydun-tagarb_200 | Aydun-tagarb_200 | 200 | Medium | GR 10.1.B 90% | I-ZAB (p7) | Master plan schematic | MP: GR 10.1.B on DN200 (PRV) from Zabda DN800 line | Yes
44 | Irb_Irb_Mar_26 | Maru | Maru | Irbid | Bushra_PS | Bushra_PS | Zabda_Res_300_G | 300 | Confirm | GR 10.3.B 44% / GR 10.3.C 39% | I-ZAB (p7) | Master plan schematic | MP: Zabda gravity DN300 -> GR 10.3.A -> PRV -> 10.3.B/C. GIS P_Zone says Bushra_PS - confirm source | No - confirm first
49 | Irb_Irb_Sal_31 | Sall-Aliya | Sall-Aliya | Irbid | Hakama_Well_9 | Hakama_Well_9 | Hakama_Well_9 |  | Confirm | GR 9.3.B 63% / GR 9.3.A 37% | I-ZAB (p7) | Master plan schematic | MP shows Zabda gravity (9.3.B DN200, 9.3.A DN350); field says independent Hakama 9 system. Ask operator | No - confirm first
51 | Irb_Irb_Al-_33 | Al-Maghayer_Zumla | Al-Maghayer_Zumla | Irbid | Rahoub_PS | Rahoub_PS | Rahoub_PS + Zabda_Res_150_G | 150 | Confirm | GR 9.3.C 67% | I-ZAB (p7) | Master plan schematic | MP: GR 9.3.C on DN150 off Zabda DN400 gravity main; remaining 33% not in any MP zone = Rahoub PS side. Split candidate | No - confirm first
71 | Maf_Nor_Hay_2 | Hay shamali | Hay shamali | North Badia | Safawi_PS | Safawi_PS_100 | Safawi_PS_100 | 100 | High | SF 100% | M-BS (p77) | Master plan schematic | Safawi PS (500 m3) pumps DN100 to SF | Yes
131 | Ajl_Ajl_Bir_2 | Bir_Dalia | Bir_Dalia | Ajlun | Samad_PS | Samad_PS_150 | Samad_PS_150 | 150 | Medium | MJ1 90% | A-SA (p56) | Master plan schematic | Samad system: MJ1 on DN100 branches off DN150 header | Yes
132 | Ajl_Ajl_Afa_3 | Afana | Afana | Ajlun | Samad_PS | Samad_PS_200 | Samad_PS_200 | 200 | Medium | MJ2 43% / RM1 20% | A-SA (p56) | Master plan schematic | MJ2 on DN100; RM1 on DN100 off DN200 header | Yes
146 | Ajl_Ajl_Afn_17 | Afna | Afna | Ajlun | Samad_PS | Samad_PS_200 | Samad_PS_200 | 200 | Medium | RM1 36% / SAM1 25% / RM2 15% | A-SA (p56) | Master plan schematic | RM1/RM2 on DN100 off DN200 header; SAM1 DN100 | Yes
149 | Ajl_Ajl_Ain_20 | Ain Janna | Ain Janna | Ajlun | Ajloun_Res_Ain_Janna_PS | Ajloun_Res_Ain_Janna_PS_150 | Ajloun_Res_Ain_Janna_PS_150 | 150 | High | AIJ5 41% / AJ2 21% / AIJ4 19% | A-KU (p52) | Master plan schematic | AJ2: Ajloun Res (953 m) gravity DN150 -> DN100; AIJ4/AIJ5: Ain Jana PS (843 m) pumped DN150 -> DN100. Split candidate | Yes
181 | Ajl_Ajl_Tha_52 | Thagret Zebaid | Thagret Zebaid | Ajlun | By_Tanks | By_Tanks | By_Tanks |  | Confirm | THZ1 76% | A-SA (p54) | Master plan schematic | MP: THZ1 on gravity DN100 network; GIS says supplied by tanks - ask operator | No - confirm first
275 | Irb_Ban_Esc_41 | Escan um Asus | Escan um Asus | Bani Ubaid |  |  | Noima_PS1_150 | 150 | Low | KE_2 9% only | I-NO1 (p19) | Master plan schematic | Weak match (9%). KE-2 fed by No'ayma PS1 DN150 + Al-Hoson booster DN150. No P_Zone in GIS - confirm | No - confirm first
280 | Irb_Nor_alm_1 | almarqes alseehi alshona line 110 | almarqes alseehi alshona line 110 | North Shouna | Al adaseeh poster | Al adaseeh poster | Moa'th Res gravity_200 | 200 | Confirm | SHN2 84% | I-TB (p27) | Master plan schematic | MP: SHN2 gravity DN200 (Mouath Res system). Field: two ways (Al-Adasiyeh booster / Moa'th Res) | No - confirm first
286 | Irb_Nor_abo_7 | abo habeel + karba balash | abo habeel + karba balash | North Shouna | Souf_PS | Souf_PS | Spairah_Well_150 | 150 | Confirm | AH 71% / WR 24% | I-MK (p23) | Master plan schematic | MP: AH fed by Spairah well DN150 + pumped DN200 main. GIS P_Zone Souf_PS looks wrong (Souf is Jarash) | No - confirm first
302 | Irb_Nor_Kri_23 | Krima aljanobia | Krima aljanobia | North Shouna | Krima aljanobia | Krima aljanobia_150 | Krima aljanobia_150 | 150 | Medium | KR2 81% | I-MK (p23) | Master plan schematic | Kraymeh PS DN150 header, DN100/125 branches | Yes
305 | Irb_Nor_sca_26 | scan krima +hay almoasasa | scan krima +hay almoasasa | North Shouna | From mkamlat PS 4,5 pumping | From mkamlat PS 4,5 pumping_100 | From mkamlat PS 4,5 pumping_100 | 100 | Medium | KR4 78% | I-MK (p23) | Master plan schematic | KR4 on DN100 from Al-Mkaymenat PS | Yes
307 | Irb_Nor_sle_28 | slekat | slekat | North Shouna | Slekat_Well | Slekat_Well_100 | Slekat_Well_100 | 100 | High | SLK 100% | I-MK (p23) | Master plan schematic | Slechat well 8 direct DN100 into SLK | Yes
315 | Maf_Maf_Tha_8 | Thagret_Al_Job | Thagret_Al_Job | Mafraq | Thagret_Al_Job+Zaatary_PS | Thagret_Al_Job_100+Zaatary_PS_300 | Thagret_Al_Job_100+Zaatary_PS_300 | 300 | High | ZA_T1 79% | M-ZAAT (p73) | Master plan schematic | AZ_T1 fed by Thaghrat Job PS DN100 and Za'atary PS DN400->DN300 - one zone, both sources | Yes
412 | Maf_Maf_Mfa_105 | Mfaradat | Mfaradat | Mafraq | Almofradat_PS | Almofradat_PS_100 | Almofradat_PS_100 | 100 | High | MO1 79% | M-DA (p63) | Master plan schematic | Al-Mofradat PS (664 m) DN100 | Yes
496 | Jar_Jar_Qaf_9 | Qafqafa | Qafqafa | Jarash | Bowidah_PS | Bowidah_PS_200 | Bowidah_PS_200 | 200 | High | QAF 97% | J-BW (p34) | Master plan schematic | Al Bwaeda PS (918 m) DN200 main to QAF | Yes
503 | Jar_Jar_Kuf_16 | Kufer kaal | Kufer kaal | Jarash | Wared_Well | Wared_Well | Wared_Well |  | Confirm | KK-6 100% | J-KF/RM (p42) | Master plan schematic | MP: KK-6 gravity DN200 from Ras Moneef Res (1180 m); field: Wared well (diesel). Ask operator | No - confirm first
529 | Jar_Jar_Alm_42 | Almarqes al sehie al qadeem | Almarqes al sehie al qadeem | Jarash | Mashtal_Fasal_PS | Mashtal_Fasal_PS_200 | Mashtal_Fasal_PS_200 | 200 | Medium | TAR-1 87% | J-JUB (p41) | Master plan schematic | Mashtal Faisal PS DN200 -> Jubba booster -> Jubba Res (722 m) gravity DN200 header to TAR-1 | Yes
573 | Jar_Jar_Bor_86 | Borma shamali gharbi | Borma shamali gharbi | Jarash | Borma_Well | Borma_Well_150 | Borma_Well_150 | 150 | Medium | BOR-1 46% / BOR-6 42% | J-BO (p38) | Master plan schematic | BOR-6 gravity DN150 (well/Borma Res); BOR-1 gravity DN100 from Borma Res (627 m) | Yes
576 | Jar_Jar_Hay_89 | Hay alskan almakroma | Hay alskan almakroma | Jarash | Borma_Well | Borma_Well_100 | Borma_Well_100 | 100 | Medium | BOR-4 93% | J-BO (p38) | Master plan schematic | BOR-4 gravity DN100 header from Borma Res | Yes
577 | Jar_Jar_nor_90 | north Borma | north Borma | Jarash | By_Tanks | By_Tanks | By_Tanks |  | Confirm | BOR-6 81% | J-BO (p38) | Master plan schematic | MP: BOR-6 gravity DN150 from Borma well line; GIS says by tanks - ask operator | No - confirm first
604 | Irb_Ram_tre_14 | treeq alturra | treeq alturra | Ramtha | Almahasie_PS | Almahasie_PS_300 | Almahasie_PS_300 | 300 | High | Al-Torrah road 69% | I-MAH (p17) | Master plan schematic | Pumped DN300 main, DN150 branch to Al-Torrah Road | Yes
620 | Maf_Maf_Dab_159 | Daba'an | Daba'an | Mafraq | Daba'an_PS | Daba'an_PS_100 | Daba'an_PS_100 | 100 | High | DN 92% | M-DA (p63) | Master plan schematic | Daba'an PS (666 m) DN100 | Yes
640 | Ajl_Ajl_San_106 | Sanaar | Sanaar | Ajlun | Samad_PS | Samad_PS_150 | Samad_PS_150 | 150 | Medium | SN1 28% / AS1 22% | A-SA (p56) | Master plan schematic | SN1 and AS1 on DN100 branches off DN150 header | Yes
644 | Irb_Irb_Alk_64 | Alkaireh | Alkaireh | Irbid | Harima_PS | Harima_PS_200 | Harima_PS_200 | 200 | High | KHYA 72% / HRM 26% | I-BAT (p9) | Master plan schematic | Harima Res PS (465 m) pumped DN200; KHYA DN125, HRM DN125 | Yes
656 | Jar_Jar_Kab_109 | Kabar_BAL | Kabar_BAL | Jarash | Bowidah_PS | Balela_Resv_150_G | Balela_Resv_150_G | 150 | High | BL-1 44% / BL-2 30% / BL-3 14% | J-BW (p34) | Master plan schematic | Balela Res (895 m) gravity DN150 -> DN100 header; Balela filled by Al Bwaeda PS DN150 | Yes
0 | Irb_Irb_Qas1 | qaser alawadieen | qaser alawadieen | Irbid |  | Hofa_Res_600_G | Hofa_Res_600_G | 600 | Medium | H_GR_4.A 78% / H_GR_01 22% | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: 600 to 400 | Yes
0 | Irb_Irb_Qas11 | almostiashfiat fadeel aldabas | almostiashfiat fadeel aldabas | Irbid |  |  | Zabda_PS_400 | 400 | Confirm | H_GR_01 100% | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: 400 to 350 from Zabda; MP: Hofa gravity | No - confirm first
0 | Irb_Irb_Qas2 | Hay ATIBa' | Hay ATIBa' | Irbid |  |  | Zabda_PS_400 | 400 | Confirm | H_GR_01 36% / Z_P_02 30% / Z_P_01 23% | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: 400 to 350; MP mixed Hofa / Zabda pumped | No - confirm first
0 | Irb_Irb_Qas13 | Zabda-Mantiqat Almadrasah | Zabda-Mantiqat Almadrasah | Irbid |  | Zabda_PS_400 | Zabda_PS_400 | 400 | Medium | Z_P_01 92% | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: 400 to 350; MP Zabda pumped (P_01 DN700 main) | Yes
0 | Irb_Irb_Qas3 | Amama bint zaynab street&Al Mustafa Mosqu | Amama bint zaynab street&Al Mustafa Mosqu | Irbid |  | Zabda_Res_800_G | Zabda_Res_800_G | 800 | High | Z_G4 84% | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: 800 gravity Zabda | Yes
0 | Irb_Irb_Qas12 | Hay Al afrah_Univercity circle | Hay Al afrah_Univercity circle | Irbid |  |  | Zabda_Res_800_G | 800 | Confirm | Z_P_02 70% / Z_G4 25% | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: gravity from 800; MP mostly Zabda pumped P_02 (DN600) | No - confirm first
0 | Irb_Irb_Qas4 | Hay Al Abrar | Hay Al Abrar | Irbid |  | Zabda_Res_800_G | Zabda_Res_800_G | 800 | High | Z_G4 85% | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: from 800 gravity | Yes
0 | Irb_Irb_Qas16 | dawaer alhokomi | dawaer alhokomi | Irbid |  | Zabda_PS_350 | Zabda_PS_350 | 350 | High | Z_P_02 84% | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: 350 pipe pumping | Yes
0 | Irb_Irb_Qas5 | qaser aladel | qaser aladel | Irbid |  | Zabda_Res_800_G | Zabda_Res_800_G | 800 | High | Z_G5 100% | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: 800 to 600 | Yes
0 | Irb_Irb_Qas14 | hadeqat alzahra and hi altlool | hadeqat alzahra and hi altlool | Irbid |  |  | Zabda_PS_600 | 600 | Confirm | Z_G5 99% | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: 600 Jida pumping Zabda; MP: Zabda gravity G5 | No - confirm first
0 | Irb_Irb_Qas6 | shari'w alhashime altal | shari'w alhashime altal | Irbid |  | Zabda_Res_800_G | Zabda_Res_800_G | 800 | High | Z_G4 86% | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: 800 to 400 | Yes
0 | Irb_Irb_Qas18 | turkoman | turkoman | Irbid |  | Zabda_Res_800_G | Zabda_Res_800_G | 800 | High | Z_G1 65% / Z_G2 33% | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: gravity 800 | Yes
0 | Irb_Irb_Qas7 | hay altoaal | hay altoaal | Irbid |  | Zabda_Res_1200_G | Zabda_Res_1200_G | 1200 | High | Z_G2 97% | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: gravity 1200 to 300 | Yes
0 | Irb_Irb_Qas15 | Albarha | Albarha | Irbid |  |  | Zabda_Res_1200_G + Zabda_PS_600 | 1200 | Confirm | Z_G3 65% / Z_G7 18% / Z_G8 15% | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: west 800+1200 gravity, east 200/600 pumping - split candidate | No - confirm first
0 | Irb_Irb_Qas8 | Hay Al Karama & Hay Aliman | Hay Al Karama & Hay Aliman | Irbid |  |  | Zabda_PS_600 | 600 | Confirm | Z_G4 89% | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: 200, 600 pumping; MP: Zabda gravity G4 | No - confirm first
0 | Irb_Irb_Qas17 | Bata Ras | Bata Ras | Irbid |  |  | Zabda_PS_600 | 600 | Confirm | mixed Z_GR_10.2.C 23% / Z_G6 18% / ... | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: 600 mm Jika pumping | No - confirm first
0 | Irb_Irb_Qas9 | Hay Al Afrah | Hay Al Afrah | Irbid |  |  | Zabda_PS_400 | 400 | Confirm | H_GR_01 55% / Z_P_01 44% | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: pumping 400 to 350 | No - confirm first
0 | Irb_Irb_Qas20 | Yarmouk University | Yarmouk University | Irbid |  | Zabda_PS_150 | Zabda_PS_150 | 150 | High | Z_P_01 97% | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: 150 pumping from Zabda | Yes
0 | Irb_Irb_Qas10 | alwoorod | alwoorod | Irbid |  |  | Zabda_PS_200 | 200 | Confirm | Z_G5 90% | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: pumping 200 from Zabda; MP gravity G5 | No - confirm first
0 | Irb_Irb_Qas19 | koliat banat Irbid | koliat banat Irbid | Irbid |  | Zabda_Res_800_G | Zabda_Res_800_G | 800 | High | Z_G5 86% | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: gravity from 800 Zabda | Yes
0 | Irb_Irb_Qas22 | hadeqat tariq and masjed | hadeqat tariq and masjed | Irbid |  |  | Zabda_PS_600 | 600 | Confirm | Z_G5 99% | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: 600 Jida pumping (Wed) + 200 pumping (Tue) | No - confirm first
0 | Irb_Irb_Qas21 | hadeqat twonis | hadeqat twonis | Irbid |  |  | Zabda_PS_600 | 600 | Confirm | Z_G5 90% | Vol II sheet I-ZAB / I-HO | Notes DN + master plan source | notes: 600 pumping Jika + 200 pumping Zabda | No - confirm first