## Operator update
id | Gov | ROU | Sub_zone | Source | P_Zone (before) | P_Zone (now) | P_Zone_changed | P_Zone recommended | Question (To_check) | Operator answer | Final answer (check_answ) | Status | Answer based on | P_zone_ver | Elev_min | Elev_Max
316 | Mafraq | Mafraq | Bweidha_Gharbiyeh | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | Bweidha_Resv_300_G | Yes | Bweidha_Resv_300_G | Check if really they by-pass the reservoir of Bweidha | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Replaces earlier note (DN100 from Bweidha PS). | Confirmed | Operator call | 1 | 857 | 915
317 | Mafraq | Mafraq | Bweidha_Oleimath | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | Bweidha_Resv_300_G | Yes | Bweidha_Resv_300_G | Check if really they by-pass the reservoir of Bweidha | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not a bypass (field note said bypass 1 bar). | Confirmed | Operator call | 1 | 828 | 878
318 | Mafraq | Mafraq | Abu_Khalaf | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | Bweidha_Resv_300_G | Yes | Bweidha_Resv_300_G | Check if really they by-pass the reservoir of Bweidha | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not a bypass (field note said bypass 1 bar). | Confirmed | Operator call | 1 | 836 | 892
319 | Mafraq | Mafraq | sahah | Bweidha_Resv_PS |  | Bweidha_Resv_BYPASS |  | Bweidha_Resv_300_G | Check if really they by-pass the reservoir of Bweidha | Not answered | Not answered by operator. All neighbouring Bweidha zones (316-326) confirmed as Bweidha Resv 12in (DN300) line -> most likely Bweidha_Resv_300_G. Ask operator. | Yes | Operator call (blank) | 0 | 815 | 861
320 | Mafraq | Mafraq | RHAb | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | Bweidha_Resv_300_G | Yes | Bweidha_Resv_300_G | Check if really they by-pass the reservoir of Bweidha | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not a bypass. | Confirmed | Operator call | 1 | 782 | 906
321 | Mafraq | Mafraq | Al_Qadam | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | Bweidha_Resv_300_G | Yes | Bweidha_Resv_300_G | Check if really they by-pass the reservoir of Bweidha | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not a bypass; field note said DN100 tap out of service. | Confirmed | Operator call | 1 | 827 | 901
322 | Mafraq | Mafraq | Ein_Bani_Hassan | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | Bweidha_Resv_300_G | Yes | Bweidha_Resv_300_G | Check if really they by-pass the reservoir of Bweidha | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not a bypass. Update GIS: DN200 Qadam->Maamaria. | Confirmed | Operator call | 1 | 624 | 890
323 | Mafraq | Mafraq | Mamarieyh | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | Bweidha_Resv_300_G | Yes | Bweidha_Resv_300_G | Check if really they by-pass the reservoir of Bweidha | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not a bypass. Update GIS: DN200 Qadam->Maamaria. | Confirmed | Operator call | 1 | 656 | 791
324 | Mafraq | Mafraq | Hamamt_Omoush | Bweidha_Resv_PS | Bweidha_Resv_300_G | Bweidha_Resv_300_G |  | Bweidha_Resv_300_G | Check from where it's fed Bwaida_Reservoir_300_gravity or Rehab_Resv ? | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not Rehab Resv. | Confirmed | Operator call | 1 | 769 | 860
325 | Mafraq | Mafraq | Hamamt-Monkhadat | Bweidha_Resv_PS | Bweidha_Resv_300_G | Bweidha_Resv_300_G |  | Bweidha_Resv_300_G | Check from where it's fed Bwaida_Reservoir_300_gravity or Rehab_Resv ? | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not Rehab Resv. | Confirmed | Operator call | 1 | 769 | 844
326 | Mafraq | Mafraq | Hamamt-Alimat | Bweidha_Resv_PS | Bweidha_Resv_300_G | Bweidha_Resv_300_G |  | Bweidha_Resv_300_G | Check from where it's fed Bwaida_Reservoir_300_gravity or Rehab_Resv ? | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not Rehab Resv. | Confirmed | Operator call | 1 | 760 | 861
327 | Mafraq | Mafraq | Dogmosseh | Dogmseh_PS | Dogmseh_PS | Dogmseh_PS |  | Dogmseh_PS | Check if fed from Dogmseh_PS or Bweida_PS | Dogmseh PS | OPERATOR: fed from Dogmseh PS (not Bweidha PS). Keep Dogmseh_PS. | Confirmed | Operator call | 1 | 736 | 851
328 | Mafraq | Mafraq | Nadrah | Dogmseh_PS | Dogmseh_PS | Dogmseh_PS |  | Dogmseh_PS | Check if fed from Dogmseh_PS or Bweida_PS | Dogmseh PS | OPERATOR: fed from Dogmseh PS (not Bweidha PS). Keep Dogmseh_PS. | Confirmed | Operator call | 1 | 763 | 819
329 | Mafraq | Mafraq | Medwar | Bweidha_Resv_PS | Bweidha_Resv_300_G | Bweidha_Resv_300_G |  | Bweidha_Resv_300_G | Check from where it's fed Bwaida_Reservoir_300_gravity or Rehab_Resv ? | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not Rehab Resv, not Qnayya PS (YWC listed Qnayya). | Confirmed | Operator call | 1 | 712 | 773
357 | Mafraq | Mafraq | Ghadeer | Za'tary | Zaatary_PS_400 | Zaatary_PS_400 |  | Zaatary_PS_400 | Check if fed from Zaatary_PS or Sumaya_PS or Hayan_booster | Zaatari PS - University pumps | OPERATOR: fed from Zaatari PS, University pumps (not Sumaya PS / Hayyan booster). Keep Zaatary_PS_400. | Confirmed | Operator call | 1 | 641 | 676
358 | Mafraq | Mafraq | Hay_Kwaytiyeh | Za'tary | Zaatary_PS_400 | Zaatary_PS_400 |  | Zaatary_PS_400 | Check if fed from Zaatary_PS or Sumaya_PS or Hayan_booster | Zaatari PS - University pumps | OPERATOR: fed from Zaatari PS, University pumps (not Sumaya PS / Hayyan booster). Keep Zaatary_PS_400. | Confirmed | Operator call | 1 | 660 | 707
369 | Mafraq | Mafraq | Al-Hudud jaber | Jaber | Jaber_Resv | Jaber_PS_100 | Yes | Jaber_PS_100 | is this area fed by the Reservoir Hudud or by Jaber PS ? | Fed from Jaber PS | OPERATOR: fed from Jaber PS, NOT Hudud Reservoir. Change P_Zone to Jaber_PS_100 (field note: DN100 from Jaber PS). Confirm line size. | Confirmed | Operator call | 1 | 571 | 598
387 | Mafraq | Mafraq | HAY ALZHOR SHARQI , SHARI ALMOHNDISIN | Sumaya | Sumaya PS_400 | Sumaya PS_400 |  | Sumaya PS_400 | Check if fe from Sumaya_PS or Hayyan_Booster ? | Main source Sumaya PS; Sunday cycle from Sumaya PS, Thursday cycle from Hayyan Booster | OPERATOR: main source Sumaya PS, but MIXED: Sunday cycle from Sumaya PS, Thursday cycle from Hayyan Booster. Keep Sumaya PS_400 (main); note Hayyan_Booster on Thursday. | Confirmed | Operator call | 1 | 689 | 727
388 | Mafraq | Mafraq | HAY NOWWARA , HAY MAQAM , HAY ALHOSBAN , HAY ALZHOR QARBI, SHARI ALMOHNDISIN | Sumaya | Sumaya PS_400 | Sumaya PS_400 |  | Sumaya PS_400 | Check if fe from Sumaya_PS or Hayyan_Booster ? | Sumaya PS | OPERATOR: fed from Sumaya PS (not Hayyan booster). Keep Sumaya PS_400. | Confirmed | Operator call | 1 | 687 | 731
389 | Mafraq | Mafraq | Hay AL HUSSEIN AND HAY FDAIN AND PART OF HAY ALTHOBAT AND HAY JEA'A | Sumaya | Sumaya PS_400 | Sumaya PS_400 |  | Sumaya PS_400 | Check if fed from Sumaya_PS or Hayyan_Booster ? | Sumaya PS | OPERATOR: fed from Sumaya PS (not Hayyan booster). Keep Sumaya PS_400. | Confirmed | Operator call | 1 | 664 | 711
390 | Mafraq | Mafraq | HAY JANOOBI AND DAHEYT KING ABDULLAH AND ESKAN | Sumaya | Sumaya PS_400 | Sumaya PS_400 |  | Sumaya PS_400 | Check if fe from Sumaya_PS or Hayyan_Booster ? | Sumaya PS | OPERATOR: fed from Sumaya PS (not Hayyan booster). Keep Sumaya PS_400. | Confirmed | Operator call | 1 | 658 | 707
391 | Mafraq | Mafraq | SOOQ HAY THOBBAT AND STREET OF JAISH | Sumaya PS | Sumaya PS_400 | Sumaya PS_200 | Yes | Sumaya PS_200 | Check if fe from Sumaya_PS or Hayyan_Booster ? | Sumaya PS | OPERATOR: fed from Sumaya PS (not Hayyan booster). Field notes: separate DN200 line direct from Sumaya PS -> Sumaya PS_200. | Confirmed | Operator call | 1 | 661 | 698
398 | Mafraq | Mafraq | Um karouba | bwida gravity | Bweidha_Resv_300_G | Bweidha_Resv_300_G |  | Bweidha_Resv_300_G | Check from where it's fed Bwaida_Reservoir_300_gravity or Rehab_Resv ? | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not Rehab Resv. | Confirmed | Operator call | 1 | 745 | 823
399 | Mafraq | Mafraq | mozareen Daqmaseh | Dogmseh_PS | Dogmseh_PS | Dogmseh_PS |  | Dogmseh_PS | Check if fed from Dogmseh_PS or Bweida_PS | Dogmseh PS, 6" line (DN150) | OPERATOR: fed from Dogmseh PS by 6in (DN150) line. Keep Dogmseh_PS. | Confirmed | Operator call | 1 | 719 | 795
413 | Mafraq | Mafraq | Hay aljeeran | Al Zubaideyeh PS | Al Zubaideyeh_PS | Al Zubaideyeh_PS_100 | Yes | Al Zubaideyeh_PS_100 | 2 discharge pipes ? if yes split the hydraulic zone | Zubaidiyeh PS, 4" steel line (DN100) | OPERATOR: Zubaidiyeh PS, 4in steel line (DN100) -> Al Zubaideyeh_PS_100. | Confirmed | Operator call | 1 | 659 | 683
414 | Mafraq | Mafraq | hay abushakir | Al Zubaideyeh PS | Al Zubaideyeh_PS | Al Zubaideyeh_PS_150 | Yes | Al Zubaideyeh_PS_150 | 2 discharge pipes ? if yes split the hydraulic zone | Zubaidiyeh PS, 6" line reduced to 4" (DN150->DN100) | OPERATOR: Zubaidiyeh PS, 6in line reduced to 4in (DN150->DN100) -> Al Zubaideyeh_PS_150. | Confirmed | Operator call | 1 | 658 | 668
415 | Mafraq | Mafraq | Hay zarafat | Al Zubaideyeh PS | Al Zubaideyeh_PS | Al Zubaideyeh_PS_100 | Yes | Al Zubaideyeh_PS_100 | 2 discharge pipes ? if yes split the hydraulic zone | Zubaidiyeh PS, 4" steel line (DN100) | OPERATOR: Zubaidiyeh PS, 4in steel line (DN100) -> Al Zubaideyeh_PS_100 (not DN125 as in field note). | Confirmed | Operator call | 1 | 663 | 675
416 | Mafraq | Mafraq | Fhailyyeh | Al Zubaideyeh PS | Al Zubaideyeh_PS | Al Zubaideyeh_PS_100 | Yes | Al Zubaideyeh_PS_100 | 2 discharge pipes ? if yes split the hydraulic zone | Zubaidiyeh PS, 4" steel line (DN100) | OPERATOR: Zubaidiyeh PS, 4in steel line (DN100) -> Al Zubaideyeh_PS_100 (not DN125 as in field note). | Confirmed | Operator call | 1 | 662 | 680
417 | Mafraq | Mafraq | Hay Nada Zbadi | Al Zubaideyeh PS | Al Zubaideyeh_PS | Zaatary_PS_100_Univ | Yes | Zaatary_PS_100_Univ | 2 discharge pipes ? if yes split the hydraulic zone | Zaatari PS, 4" line (DN100) from University pump | OPERATOR: NOT Zubaidiyeh PS - fed from Zaatari PS, 4in line (DN100) from the University pump. Change P_Zone to Zaatary_PS_100_Univ. | Confirmed | Operator call | 1 | 660 | 678
418 | Mafraq | Mafraq | Tareeq Al Nahdah | Al Zubaideyeh PS | Al Zubaideyeh_PS | BAEJ_PS_100 | Yes | BAEJ_PS_100 | 2 discharge pipes ? if yes split the hydraulic zone | Baej PS, 4" steel line (DN100) | OPERATOR: NOT Zubaidiyeh PS - fed from Baej PS, 4in steel line (DN100). Confirm Baej 2 or Baej 3, then set BAEJ 2_PS_100 or BAEJ 3_PS. | Confirm | Operator call | 0 | 653 | 680
419 | Mafraq | Mafraq | Hwajah and Hay alamerah Hya | Al Zubaideyeh PS | Al Zubaideyeh_PS | Al Zubaideyeh_PS_100 | Yes | Al Zubaideyeh_PS_100 | 2 discharge pipes ? if yes split the hydraulic zone | Zubaidiyeh PS, 4" steel line (DN100); Hay Al Amira on 2" line (DN50) | OPERATOR: Zubaidiyeh PS, 4in steel line (DN100); Hay Al Amira on a 2in (DN50) branch -> Al Zubaideyeh_PS_100. | Confirmed | Operator call | 1 | 636 | 671
420 | Mafraq | Mafraq | Hay Albaladiyyeh | Um EsSerb PS | Um EsSerb PS | Um EsSerb PS_100 | Yes | Um EsSerb PS_100 | is there 2 discharge from the PS 100 + 150 ? PS Um-Serb PS feed Zubeydeh PS or invers ? | Um Serb PS, 4" steel line (DN100) | OPERATOR: Um Serb PS, 4in steel line (DN100) -> Um EsSerb PS_100. Um Serb <-> Zubaidiyeh direction still not answered. | Confirmed | Operator call | 1 | 642 | 654
421 | Mafraq | Mafraq | Al wasit and tareeq samp alsarhan | Um EsSerb PS | Um EsSerb PS | Um EsSerb PS_150 | Yes | Um EsSerb PS_150 | is there 2 discharge from the PS 100 + 150 ? PS Um-Serb PS feed Zubeydeh PS or invers ? | Um Serb PS, DN150-100-63 line (part steel, part PE) | OPERATOR: Um Serb PS, DN150 -> 100 -> 63 line (part steel, part PE) -> Um EsSerb PS_150. | Confirmed | Operator call | 1 | 645 | 663
422 | Mafraq | Mafraq | Rawded Rowayei | Um EsSerb PS | Um EsSerb PS | Um EsSerb PS_100 | Yes | Um EsSerb PS_100 | is there 2 discharge from the PS 100 + 150 ? PS Um-Serb PS feed Zubeydeh PS or invers ? | Um Serb PS, 4" line (DN100) | OPERATOR: Um Serb PS, 4in line (DN100) -> Um EsSerb PS_100. | Confirmed | Operator call | 1 | 646 | 669
423 | Mafraq | Mafraq | Sawalah | Um EsSerb PS | Um EsSerb PS | Um EsSerb PS_100 | Yes | Um EsSerb PS_100 | is there 2 discharge from the PS 100 + 150 ? PS Um-Serb PS feed Zubeydeh PS or invers ? | Um Serb PS, 4" PE line (DN100), Thu evening to Fri morning | OPERATOR: Um Serb PS, 4in PE line (DN100), supply Thu evening to Fri morning -> Um EsSerb PS_100. | Confirmed | Operator call | 1 | 642 | 667
424 | Mafraq | Mafraq | Nahdah | Um EsSerb PS | Um EsSerb PS | Um EsSerb PS_100 | Yes | Um EsSerb PS_100 | is there 2 discharge from the PS 100 + 150 ? PS Um-Serb PS feed Zubeydeh PS or invers ? | Um Serb PS, 4" line (DN100), Tuesday and Wednesday | OPERATOR: Um Serb PS, 4in line (DN100), supply Tue and Wed -> Um EsSerb PS_100 (not DN150 as in field note). | Confirmed | Operator call | 1 | 650 | 675
439 | Mafraq | Mafraq | Jabal anoor phase 1 | Balaama PS | Balaama_PS | Balaama_Resv_250_G | Yes | Balaama_Resv_250_G | check if fed by DN200 from Balaama Resv by gravity ? or from Znayah PS ? | Balaama Reservoir by gravity, 10" line (DN250) | OPERATOR: fed by gravity from Balaama Reservoir, 10in line (DN250), not Znayah PS -> Balaama_Resv_250_G. | Confirmed | Operator call | 1 | 655 | 711
447 | Mafraq | Mafraq | Hay AGGAD and Balaama Hay shamali | Zeenah PS | Znayah_PS_200 | Znayah_PS_200 |  | Znayah_PS_200 + Balaama_Resv_250_G | check if fed by DN200 from Balaama Resv by gravity ? or from Znayah PS_DN200 ? | Part from Balaama Reservoir, part from Znayah PS | OPERATOR: mixed - part from Balaama Reservoir (gravity), part from Znayah PS. Split polygon: Hay Aggad -> Balaama_Resv_250_G, Balaama Hay Shamali -> Znayah_PS_200. | Split | Operator call | 0 | 650 | 763
448 | Mafraq | Mafraq | Mortafaat Balaama (Jabal alnaar old netowrk) | Zeenah PS | Znayah_PS_200 | Znayah_PS_200 |  | Znayah_PS_200 | check if fed by DN200 from Balaama Resv by gravity ? or from Znayah PS_DN200 ? | Znayah PS (pumped) | OPERATOR: pumped from Znayah PS (not Balaama gravity). Keep Znayah_PS_200. | Confirmed | Operator call | 1 | 664 | 710
454 | Mafraq | Mafraq | Baej Hay Janoobi Gharbi | BAEJ 2 PS | BAEJ 2_PS | BAEJ 2_PS_150 | Yes | BAEJ 2_PS_150 | Check if really from Baaj_PS_2 ? how many discharge lines ? if more then 1 split the hydraulic zone. | Baej PS, 6" line (DN150) | OPERATOR: Baej PS, 6in line (DN150). Baej 2 has one DN150 line -> no split needed. BAEJ 2_PS_150. | Confirmed | Operator call | 1 | 662 | 681
455 | Mafraq | Mafraq | BAEJ HAY JANOOBI | BAEJ 2 PS | BAEJ 2_PS | BAEJ 2_PS_150 | Yes | BAEJ 2_PS_150 | Check if really from Baaj_PS_2 ? how many discharge lines ? if more then 1 split the hydraulic zone. | Baej PS, 6" line (DN150) | OPERATOR: Baej PS, 6in line (DN150). Baej 2 has one DN150 line -> no split needed. BAEJ 2_PS_150. | Confirmed | Operator call | 1 | 659 | 679
456 | Mafraq | Mafraq | Baej Hay Gharbi | BAEJ 2 PS | BAEJ 2_PS | BAEJ 2_PS_150 | Yes | BAEJ 2_PS_150 | Check if really from Baaj_PS_2 ? how many discharge lines ? if more then 1 split the hydraulic zone. | Baej PS, 6" line (DN150) | OPERATOR: Baej PS, 6in line (DN150). Baej 2 has one DN150 line -> no split needed. BAEJ 2_PS_150. | Confirmed | Operator call | 1 | 666 | 678
457 | Mafraq | Mafraq | Baej Hay SHAMALI | BAEJ 2 PS | BAEJ 2_PS | BAEJ 2_PS_150 | Yes | BAEJ 2_PS_150 | Check if really from Baaj_PS_2 ? how many discharge lines ? if more then 1 split the hydraulic zone. | Baej PS | OPERATOR: Baej PS (line size not given; neighbours on 6in DN150 line) -> BAEJ 2_PS_150. | Confirmed | Operator call | 1 | 669 | 685
458 | Mafraq | Mafraq | Hay Al Mebrek and Hay al ATHAR | BAEJ 2 PS | BAEJ 2_PS | BAEJ 2_PS_150 | Yes | BAEJ 2_PS_150 | Check if really from Baaj_PS_2 ? how many discharge lines ? if more then 1 split the hydraulic zone. | Baej PS, 6" reduced to 2" (DN150->DN50) | OPERATOR: Baej PS, 6in line reduced to 2in (DN150->DN50). BAEJ 2_PS_150. | Confirmed | Operator call | 1 | 672 | 691
459 | Mafraq | Mafraq | BEDAYAT TAREEQ MESHIREF | BAEJ 3 PS | BAEJ 3_PS | BAEJ 3_PS |  | BAEJ 3_PS | To check with operator if realy from Baaj PS 3 ? how many discharge ? | Baej PS, 4" steel line (DN100) | OPERATOR: Baej PS, 4in steel line (DN100). One line -> no split. Keep BAEJ 3_PS. | Confirmed | Operator call | 1 | 667 | 684
460 | Mafraq | Mafraq | Mehrif Hay shamali | BAEJ 3 PS | BAEJ 3_PS | BAEJ 3_PS |  | BAEJ 3_PS | To check with operator if realy from Baaj PS 3 ? how many discharge ? | Meshref PS, 4" steel line (DN100) | OPERATOR: 'Meshref PS', 4in steel line (DN100). Most likely Baej 3 PS (the PS at Meshref road). Keep BAEJ 3_PS - confirm the name. | Confirm | Operator call | 0 | 672 | 700
461 | Mafraq | Mafraq | Hosha | Hosha_Booster | Hosha_Booster_150 | Hosha_Booster_150 |  | Hosha_Booster_150 | Fed by Hosha booster ? or um Lulu ps ? | Hosha Booster | OPERATOR: fed from Hosha Booster (not Um Lulu PS). Keep Hosha_Booster_150. | Confirmed | Operator call | 1 | 619 | 735
462 | Mafraq | Mafraq | Hamnanah , Bostanah and part of Um SWEIneh | Balama PS | Znayah_PS_200 | Znayah_PS_200 |  | Znayah_PS_200 | check if fed by DN200 from Balaama Resv by gravity ? or from Znayah PS_DN200 ? | Znayah PS | OPERATOR: fed from Znayah PS (not Balaama gravity). Keep Znayah_PS_200; line size not given (field note: DN180 + DN300). | Confirmed | Operator call | 1 | 641 | 707
623 | Mafraq | Mafraq | Um_Butaimah | Dogmseh_PS | Dogmseh_PS | Dogmseh_PS |  | Dogmseh_PS | Check if fed from Dogmseh_PS or Bweida_PS | Dogmseh PS, 6" line (DN150) | OPERATOR: fed from Dogmseh PS by 6in (DN150) line. Keep Dogmseh_PS. | Confirmed | Operator call | 1 | 765 | 936
624 | Mafraq | Mafraq | Hweishan | Dogmseh_PS | Dogmseh_PS | Dogmseh_PS |  | Dogmseh_PS | Check if fed from Dogmseh_PS or Bweida_PS | Dogmseh PS, 6" line (DN150) | OPERATOR: fed from Dogmseh PS by 6in (DN150) line (YWC listed Bwaidah PS = origin of water). Keep Dogmseh_PS. | Confirmed | Operator call | 1 | 736 | 882
625 | Mafraq | Mafraq | Ein AL Nabi | Dogmseh_PS | Dogmseh_PS | Dogmseh_PS |  | Dogmseh_PS | Check if fed from Dogmseh_PS or Bweida_PS | Dogmseh PS, 6" line (DN150) | OPERATOR: fed from Dogmseh PS by 6in (DN150) line (YWC listed Bwaidah PS = origin of water). Keep Dogmseh_PS. | Confirmed | Operator call | 1 | 685 | 803
655 | Mafraq | Mafraq | Tareeq Koum Ahmar | Koum ahmar ps | Koum Ahmar_PS | Koum Ahmar_PS_150 | Yes | Koum Ahmar_PS_150 | How many discharge lines ? split the hydraulic zone | Koum Ahmar PS, 6" line (DN150) | OPERATOR: Koum Ahmar PS, 6in line (DN150) -> Koum Ahmar_PS_150. | Confirmed | Operator call | 1 | 676 | 704

## All 69 checks
id | Gov | ROU | Sub_zone | Source | P_Zone (before) | P_Zone (now) | P_Zone_changed | P_Zone recommended | Question (To_check) | Operator answer | Final answer (check_answ) | Status | Answer based on | P_zone_ver | Elev_min | Elev_Max
72 | Mafraq | North Badia | Hashmyye/Alyah shwee'er/ Manshiyyet khaleefa /slaah JAW | K140 PS |  | Safawi_PS |  | K140_PS | CHECK the pressure zone - if K140 or Safawi ? are theses two facilities connected ? |  | K140_PS (not Safawi). K140 PS lies inside this zone, Safawi PS ~25 km away. Area tapped DN100/63 on DN400 main from wells K136+K140 (YWC src: wells 136+140, Safawi WS) - same system, pressure from K140 side. | No | Data analysis | 0 | 775 | 820
74 | Mafraq | North Badia | Dir Al-Kahf | Beshryyeh PS |  | Bishiryyah_PS |  | Bishiryyah_PS | TO CHECK IF FROM Beshryyeh PS or Dir Al kahf PS ? |  | Beshryyeh PS - keep Bishiryyah_PS. Field: DN200 from Beshryyeh PS (main filling Dir Al-Kahf tank). Dir Al-Kahf PS sits in this zone (990-1067m) but its pumps H=250m serve upper villages (id75). YWC names Dair Al Kahef PS | Confirm | Data analysis | 0 | 990 | 1067
75 | Mafraq | North Badia | Tal Rmah,Mrajb, deir al qen ,jadaa,Mathnah , mansoora | Dr Al-kahf PS |  | Dir Al-kahf PS |  | Dir Al-kahf PS | Check if the resv Dair Al Qenn is used ? or bypassed ? if used how ? |  | Dair Al Qenn Resv NOT used - bypassed (Master plan: Dir Al-Qun Resv = Abandoned). Fed directly by DN150 from Dir Al-Kahf PS (YWC confirms). YWC has 2 schedules: Tal Rmah / Deir Al Qen+Jadaa+Mathnah+Mansoora | No | Data analysis | 1 | 1071 | 1174
97 | Mafraq | North Badia | Koum Ahmar Hay shamali and Janoobi | Koum Ahmar ps |  | Koum Ahmar_PS |  | Koum Ahmar_PS_125 | How many discharge lines ? split the hydraulic zone |  | Koum Ahmar PS has 2 pumps (50m3/h@250m, 100m3/h@100m) and 2 distribution outlets DN125 + DN100 (field notes). This zone fed by DN125 (+DN100) -> Koum Ahmar_PS_125. Confirm which pump feeds which line. | Confirm | Data analysis | 0 | 696 | 750
98 | Mafraq | North Badia | MANSHIYYET ALKAMEES | Koum Ahmar ps |  | Koum Ahmar_PS |  | Koum Ahmar_PS_100 | How many discharge lines ? split the hydraulic zone |  | Koum Ahmar PS has 2 pumps (50m3/h@250m, 100m3/h@100m) and 2 distribution outlets DN125 + DN100 (field notes). This zone fed by DN100 -> Koum Ahmar_PS_100. Confirm which pump feeds which line. | Confirm | Data analysis | 0 | 727 | 761
99 | Mafraq | North Badia | Rasm Alhesan | Koum Ahmar ps |  | Koum Ahmar_PS |  | Koum Ahmar_PS_100 | How many discharge lines ? split the hydraulic zone |  | Koum Ahmar PS has 2 pumps (50m3/h@250m, 100m3/h@100m) and 2 distribution outlets DN125 + DN100 (field notes). This zone fed by DN100 -> Koum Ahmar_PS_100. Confirm which pump feeds which line. | Confirm | Data analysis | 0 | 744 | 766
100 | Mafraq | North Badia | Hay Al Joulan | Koum Ahmar ps |  | Koum Ahmar_PS |  | Koum Ahmar_PS_100 | How many discharge lines ? split the hydraulic zone |  | Koum Ahmar PS has 2 pumps (50m3/h@250m, 100m3/h@100m) and 2 distribution outlets DN125 + DN100 (field notes). Zone fed by DN100 (+DN50) -> Koum Ahmar_PS_100. GIS network differs - update. | Confirm | Data analysis | 0 | 702 | 720
316 | Mafraq | Mafraq | Bweidha_Gharbiyeh | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | Bweidha_Resv_300_G | Yes | Bweidha_Resv_300_G | Check if really they by-pass the reservoir of Bweidha | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Replaces earlier note (DN100 from Bweidha PS). | Confirmed | Operator call | 1 | 857 | 915
317 | Mafraq | Mafraq | Bweidha_Oleimath | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | Bweidha_Resv_300_G | Yes | Bweidha_Resv_300_G | Check if really they by-pass the reservoir of Bweidha | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not a bypass (field note said bypass 1 bar). | Confirmed | Operator call | 1 | 828 | 878
318 | Mafraq | Mafraq | Abu_Khalaf | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | Bweidha_Resv_300_G | Yes | Bweidha_Resv_300_G | Check if really they by-pass the reservoir of Bweidha | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not a bypass (field note said bypass 1 bar). | Confirmed | Operator call | 1 | 836 | 892
319 | Mafraq | Mafraq | sahah | Bweidha_Resv_PS |  | Bweidha_Resv_BYPASS |  | Bweidha_Resv_300_G | Check if really they by-pass the reservoir of Bweidha | Not answered | Not answered by operator. All neighbouring Bweidha zones (316-326) confirmed as Bweidha Resv 12in (DN300) line -> most likely Bweidha_Resv_300_G. Ask operator. | Yes | Operator call (blank) | 0 | 815 | 861
320 | Mafraq | Mafraq | RHAb | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | Bweidha_Resv_300_G | Yes | Bweidha_Resv_300_G | Check if really they by-pass the reservoir of Bweidha | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not a bypass. | Confirmed | Operator call | 1 | 782 | 906
321 | Mafraq | Mafraq | Al_Qadam | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | Bweidha_Resv_300_G | Yes | Bweidha_Resv_300_G | Check if really they by-pass the reservoir of Bweidha | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not a bypass; field note said DN100 tap out of service. | Confirmed | Operator call | 1 | 827 | 901
322 | Mafraq | Mafraq | Ein_Bani_Hassan | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | Bweidha_Resv_300_G | Yes | Bweidha_Resv_300_G | Check if really they by-pass the reservoir of Bweidha | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not a bypass. Update GIS: DN200 Qadam->Maamaria. | Confirmed | Operator call | 1 | 624 | 890
323 | Mafraq | Mafraq | Mamarieyh | Bweidha_Resv_PS | Bweidha_Resv_BYPASS | Bweidha_Resv_300_G | Yes | Bweidha_Resv_300_G | Check if really they by-pass the reservoir of Bweidha | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not a bypass. Update GIS: DN200 Qadam->Maamaria. | Confirmed | Operator call | 1 | 656 | 791
324 | Mafraq | Mafraq | Hamamt_Omoush | Bweidha_Resv_PS | Bweidha_Resv_300_G | Bweidha_Resv_300_G |  | Bweidha_Resv_300_G | Check from where it's fed Bwaida_Reservoir_300_gravity or Rehab_Resv ? | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not Rehab Resv. | Confirmed | Operator call | 1 | 769 | 860
325 | Mafraq | Mafraq | Hamamt-Monkhadat | Bweidha_Resv_PS | Bweidha_Resv_300_G | Bweidha_Resv_300_G |  | Bweidha_Resv_300_G | Check from where it's fed Bwaida_Reservoir_300_gravity or Rehab_Resv ? | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not Rehab Resv. | Confirmed | Operator call | 1 | 769 | 844
326 | Mafraq | Mafraq | Hamamt-Alimat | Bweidha_Resv_PS | Bweidha_Resv_300_G | Bweidha_Resv_300_G |  | Bweidha_Resv_300_G | Check from where it's fed Bwaida_Reservoir_300_gravity or Rehab_Resv ? | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not Rehab Resv. | Confirmed | Operator call | 1 | 760 | 861
327 | Mafraq | Mafraq | Dogmosseh | Dogmseh_PS | Dogmseh_PS | Dogmseh_PS |  | Dogmseh_PS | Check if fed from Dogmseh_PS or Bweida_PS | Dogmseh PS | OPERATOR: fed from Dogmseh PS (not Bweidha PS). Keep Dogmseh_PS. | Confirmed | Operator call | 1 | 736 | 851
328 | Mafraq | Mafraq | Nadrah | Dogmseh_PS | Dogmseh_PS | Dogmseh_PS |  | Dogmseh_PS | Check if fed from Dogmseh_PS or Bweida_PS | Dogmseh PS | OPERATOR: fed from Dogmseh PS (not Bweidha PS). Keep Dogmseh_PS. | Confirmed | Operator call | 1 | 763 | 819
329 | Mafraq | Mafraq | Medwar | Bweidha_Resv_PS | Bweidha_Resv_300_G | Bweidha_Resv_300_G |  | Bweidha_Resv_300_G | Check from where it's fed Bwaida_Reservoir_300_gravity or Rehab_Resv ? | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not Rehab Resv, not Qnayya PS (YWC listed Qnayya). | Confirmed | Operator call | 1 | 712 | 773
357 | Mafraq | Mafraq | Ghadeer | Za'tary | Zaatary_PS_400 | Zaatary_PS_400 |  | Zaatary_PS_400 | Check if fed from Zaatary_PS or Sumaya_PS or Hayan_booster | Zaatari PS - University pumps | OPERATOR: fed from Zaatari PS, University pumps (not Sumaya PS / Hayyan booster). Keep Zaatary_PS_400. | Confirmed | Operator call | 1 | 641 | 676
358 | Mafraq | Mafraq | Hay_Kwaytiyeh | Za'tary | Zaatary_PS_400 | Zaatary_PS_400 |  | Zaatary_PS_400 | Check if fed from Zaatary_PS or Sumaya_PS or Hayan_booster | Zaatari PS - University pumps | OPERATOR: fed from Zaatari PS, University pumps (not Sumaya PS / Hayyan booster). Keep Zaatary_PS_400. | Confirmed | Operator call | 1 | 660 | 707
369 | Mafraq | Mafraq | Al-Hudud jaber | Jaber | Jaber_Resv | Jaber_PS_100 | Yes | Jaber_PS_100 | is this area fed by the Reservoir Hudud or by Jaber PS ? | Fed from Jaber PS | OPERATOR: fed from Jaber PS, NOT Hudud Reservoir. Change P_Zone to Jaber_PS_100 (field note: DN100 from Jaber PS). Confirm line size. | Confirmed | Operator call | 1 | 571 | 598
387 | Mafraq | Mafraq | HAY ALZHOR SHARQI , SHARI ALMOHNDISIN | Sumaya | Sumaya PS_400 | Sumaya PS_400 |  | Sumaya PS_400 | Check if fe from Sumaya_PS or Hayyan_Booster ? | Main source Sumaya PS; Sunday cycle from Sumaya PS, Thursday cycle from Hayyan Booster | OPERATOR: main source Sumaya PS, but MIXED: Sunday cycle from Sumaya PS, Thursday cycle from Hayyan Booster. Keep Sumaya PS_400 (main); note Hayyan_Booster on Thursday. | Confirmed | Operator call | 1 | 689 | 727
388 | Mafraq | Mafraq | HAY NOWWARA , HAY MAQAM , HAY ALHOSBAN , HAY ALZHOR QARBI, SHARI ALMOHNDISIN | Sumaya | Sumaya PS_400 | Sumaya PS_400 |  | Sumaya PS_400 | Check if fe from Sumaya_PS or Hayyan_Booster ? | Sumaya PS | OPERATOR: fed from Sumaya PS (not Hayyan booster). Keep Sumaya PS_400. | Confirmed | Operator call | 1 | 687 | 731
389 | Mafraq | Mafraq | Hay AL HUSSEIN AND HAY FDAIN AND PART OF HAY ALTHOBAT AND HAY JEA'A | Sumaya | Sumaya PS_400 | Sumaya PS_400 |  | Sumaya PS_400 | Check if fed from Sumaya_PS or Hayyan_Booster ? | Sumaya PS | OPERATOR: fed from Sumaya PS (not Hayyan booster). Keep Sumaya PS_400. | Confirmed | Operator call | 1 | 664 | 711
390 | Mafraq | Mafraq | HAY JANOOBI AND DAHEYT KING ABDULLAH AND ESKAN | Sumaya | Sumaya PS_400 | Sumaya PS_400 |  | Sumaya PS_400 | Check if fe from Sumaya_PS or Hayyan_Booster ? | Sumaya PS | OPERATOR: fed from Sumaya PS (not Hayyan booster). Keep Sumaya PS_400. | Confirmed | Operator call | 1 | 658 | 707
391 | Mafraq | Mafraq | SOOQ HAY THOBBAT AND STREET OF JAISH | Sumaya PS | Sumaya PS_400 | Sumaya PS_200 | Yes | Sumaya PS_200 | Check if fe from Sumaya_PS or Hayyan_Booster ? | Sumaya PS | OPERATOR: fed from Sumaya PS (not Hayyan booster). Field notes: separate DN200 line direct from Sumaya PS -> Sumaya PS_200. | Confirmed | Operator call | 1 | 661 | 698
398 | Mafraq | Mafraq | Um karouba | bwida gravity | Bweidha_Resv_300_G | Bweidha_Resv_300_G |  | Bweidha_Resv_300_G | Check from where it's fed Bwaida_Reservoir_300_gravity or Rehab_Resv ? | Bweidha Reservoir, 12" line (DN300) | OPERATOR: fed from Bweidha Reservoir by the 12in (DN300) line -> reservoir IS used, gravity DN300. P_Zone = Bweidha_Resv_300_G. Not Rehab Resv. | Confirmed | Operator call | 1 | 745 | 823
399 | Mafraq | Mafraq | mozareen Daqmaseh | Dogmseh_PS | Dogmseh_PS | Dogmseh_PS |  | Dogmseh_PS | Check if fed from Dogmseh_PS or Bweida_PS | Dogmseh PS, 6" line (DN150) | OPERATOR: fed from Dogmseh PS by 6in (DN150) line. Keep Dogmseh_PS. | Confirmed | Operator call | 1 | 719 | 795
413 | Mafraq | Mafraq | Hay aljeeran | Al Zubaideyeh PS | Al Zubaideyeh_PS | Al Zubaideyeh_PS_100 | Yes | Al Zubaideyeh_PS_100 | 2 discharge pipes ? if yes split the hydraulic zone | Zubaidiyeh PS, 4" steel line (DN100) | OPERATOR: Zubaidiyeh PS, 4in steel line (DN100) -> Al Zubaideyeh_PS_100. | Confirmed | Operator call | 1 | 659 | 683
414 | Mafraq | Mafraq | hay abushakir | Al Zubaideyeh PS | Al Zubaideyeh_PS | Al Zubaideyeh_PS_150 | Yes | Al Zubaideyeh_PS_150 | 2 discharge pipes ? if yes split the hydraulic zone | Zubaidiyeh PS, 6" line reduced to 4" (DN150->DN100) | OPERATOR: Zubaidiyeh PS, 6in line reduced to 4in (DN150->DN100) -> Al Zubaideyeh_PS_150. | Confirmed | Operator call | 1 | 658 | 668
415 | Mafraq | Mafraq | Hay zarafat | Al Zubaideyeh PS | Al Zubaideyeh_PS | Al Zubaideyeh_PS_100 | Yes | Al Zubaideyeh_PS_100 | 2 discharge pipes ? if yes split the hydraulic zone | Zubaidiyeh PS, 4" steel line (DN100) | OPERATOR: Zubaidiyeh PS, 4in steel line (DN100) -> Al Zubaideyeh_PS_100 (not DN125 as in field note). | Confirmed | Operator call | 1 | 663 | 675
416 | Mafraq | Mafraq | Fhailyyeh | Al Zubaideyeh PS | Al Zubaideyeh_PS | Al Zubaideyeh_PS_100 | Yes | Al Zubaideyeh_PS_100 | 2 discharge pipes ? if yes split the hydraulic zone | Zubaidiyeh PS, 4" steel line (DN100) | OPERATOR: Zubaidiyeh PS, 4in steel line (DN100) -> Al Zubaideyeh_PS_100 (not DN125 as in field note). | Confirmed | Operator call | 1 | 662 | 680
417 | Mafraq | Mafraq | Hay Nada Zbadi | Al Zubaideyeh PS | Al Zubaideyeh_PS | Zaatary_PS_100_Univ | Yes | Zaatary_PS_100_Univ | 2 discharge pipes ? if yes split the hydraulic zone | Zaatari PS, 4" line (DN100) from University pump | OPERATOR: NOT Zubaidiyeh PS - fed from Zaatari PS, 4in line (DN100) from the University pump. Change P_Zone to Zaatary_PS_100_Univ. | Confirmed | Operator call | 1 | 660 | 678
418 | Mafraq | Mafraq | Tareeq Al Nahdah | Al Zubaideyeh PS | Al Zubaideyeh_PS | BAEJ_PS_100 | Yes | BAEJ_PS_100 | 2 discharge pipes ? if yes split the hydraulic zone | Baej PS, 4" steel line (DN100) | OPERATOR: NOT Zubaidiyeh PS - fed from Baej PS, 4in steel line (DN100). Confirm Baej 2 or Baej 3, then set BAEJ 2_PS_100 or BAEJ 3_PS. | Confirm | Operator call | 0 | 653 | 680
419 | Mafraq | Mafraq | Hwajah and Hay alamerah Hya | Al Zubaideyeh PS | Al Zubaideyeh_PS | Al Zubaideyeh_PS_100 | Yes | Al Zubaideyeh_PS_100 | 2 discharge pipes ? if yes split the hydraulic zone | Zubaidiyeh PS, 4" steel line (DN100); Hay Al Amira on 2" line (DN50) | OPERATOR: Zubaidiyeh PS, 4in steel line (DN100); Hay Al Amira on a 2in (DN50) branch -> Al Zubaideyeh_PS_100. | Confirmed | Operator call | 1 | 636 | 671
420 | Mafraq | Mafraq | Hay Albaladiyyeh | Um EsSerb PS | Um EsSerb PS | Um EsSerb PS_100 | Yes | Um EsSerb PS_100 | is there 2 discharge from the PS 100 + 150 ? PS Um-Serb PS feed Zubeydeh PS or invers ? | Um Serb PS, 4" steel line (DN100) | OPERATOR: Um Serb PS, 4in steel line (DN100) -> Um EsSerb PS_100. Um Serb <-> Zubaidiyeh direction still not answered. | Confirmed | Operator call | 1 | 642 | 654
421 | Mafraq | Mafraq | Al wasit and tareeq samp alsarhan | Um EsSerb PS | Um EsSerb PS | Um EsSerb PS_150 | Yes | Um EsSerb PS_150 | is there 2 discharge from the PS 100 + 150 ? PS Um-Serb PS feed Zubeydeh PS or invers ? | Um Serb PS, DN150-100-63 line (part steel, part PE) | OPERATOR: Um Serb PS, DN150 -> 100 -> 63 line (part steel, part PE) -> Um EsSerb PS_150. | Confirmed | Operator call | 1 | 645 | 663
422 | Mafraq | Mafraq | Rawded Rowayei | Um EsSerb PS | Um EsSerb PS | Um EsSerb PS_100 | Yes | Um EsSerb PS_100 | is there 2 discharge from the PS 100 + 150 ? PS Um-Serb PS feed Zubeydeh PS or invers ? | Um Serb PS, 4" line (DN100) | OPERATOR: Um Serb PS, 4in line (DN100) -> Um EsSerb PS_100. | Confirmed | Operator call | 1 | 646 | 669
423 | Mafraq | Mafraq | Sawalah | Um EsSerb PS | Um EsSerb PS | Um EsSerb PS_100 | Yes | Um EsSerb PS_100 | is there 2 discharge from the PS 100 + 150 ? PS Um-Serb PS feed Zubeydeh PS or invers ? | Um Serb PS, 4" PE line (DN100), Thu evening to Fri morning | OPERATOR: Um Serb PS, 4in PE line (DN100), supply Thu evening to Fri morning -> Um EsSerb PS_100. | Confirmed | Operator call | 1 | 642 | 667
424 | Mafraq | Mafraq | Nahdah | Um EsSerb PS | Um EsSerb PS | Um EsSerb PS_100 | Yes | Um EsSerb PS_100 | is there 2 discharge from the PS 100 + 150 ? PS Um-Serb PS feed Zubeydeh PS or invers ? | Um Serb PS, 4" line (DN100), Tuesday and Wednesday | OPERATOR: Um Serb PS, 4in line (DN100), supply Tue and Wed -> Um EsSerb PS_100 (not DN150 as in field note). | Confirmed | Operator call | 1 | 650 | 675
439 | Mafraq | Mafraq | Jabal anoor phase 1 | Balaama PS | Balaama_PS | Balaama_Resv_250_G | Yes | Balaama_Resv_250_G | check if fed by DN200 from Balaama Resv by gravity ? or from Znayah PS ? | Balaama Reservoir by gravity, 10" line (DN250) | OPERATOR: fed by gravity from Balaama Reservoir, 10in line (DN250), not Znayah PS -> Balaama_Resv_250_G. | Confirmed | Operator call | 1 | 655 | 711
447 | Mafraq | Mafraq | Hay AGGAD and Balaama Hay shamali | Zeenah PS | Znayah_PS_200 | Znayah_PS_200 |  | Znayah_PS_200 + Balaama_Resv_250_G | check if fed by DN200 from Balaama Resv by gravity ? or from Znayah PS_DN200 ? | Part from Balaama Reservoir, part from Znayah PS | OPERATOR: mixed - part from Balaama Reservoir (gravity), part from Znayah PS. Split polygon: Hay Aggad -> Balaama_Resv_250_G, Balaama Hay Shamali -> Znayah_PS_200. | Split | Operator call | 0 | 650 | 763
448 | Mafraq | Mafraq | Mortafaat Balaama (Jabal alnaar old netowrk) | Zeenah PS | Znayah_PS_200 | Znayah_PS_200 |  | Znayah_PS_200 | check if fed by DN200 from Balaama Resv by gravity ? or from Znayah PS_DN200 ? | Znayah PS (pumped) | OPERATOR: pumped from Znayah PS (not Balaama gravity). Keep Znayah_PS_200. | Confirmed | Operator call | 1 | 664 | 710
454 | Mafraq | Mafraq | Baej Hay Janoobi Gharbi | BAEJ 2 PS | BAEJ 2_PS | BAEJ 2_PS_150 | Yes | BAEJ 2_PS_150 | Check if really from Baaj_PS_2 ? how many discharge lines ? if more then 1 split the hydraulic zone. | Baej PS, 6" line (DN150) | OPERATOR: Baej PS, 6in line (DN150). Baej 2 has one DN150 line -> no split needed. BAEJ 2_PS_150. | Confirmed | Operator call | 1 | 662 | 681
455 | Mafraq | Mafraq | BAEJ HAY JANOOBI | BAEJ 2 PS | BAEJ 2_PS | BAEJ 2_PS_150 | Yes | BAEJ 2_PS_150 | Check if really from Baaj_PS_2 ? how many discharge lines ? if more then 1 split the hydraulic zone. | Baej PS, 6" line (DN150) | OPERATOR: Baej PS, 6in line (DN150). Baej 2 has one DN150 line -> no split needed. BAEJ 2_PS_150. | Confirmed | Operator call | 1 | 659 | 679
456 | Mafraq | Mafraq | Baej Hay Gharbi | BAEJ 2 PS | BAEJ 2_PS | BAEJ 2_PS_150 | Yes | BAEJ 2_PS_150 | Check if really from Baaj_PS_2 ? how many discharge lines ? if more then 1 split the hydraulic zone. | Baej PS, 6" line (DN150) | OPERATOR: Baej PS, 6in line (DN150). Baej 2 has one DN150 line -> no split needed. BAEJ 2_PS_150. | Confirmed | Operator call | 1 | 666 | 678
457 | Mafraq | Mafraq | Baej Hay SHAMALI | BAEJ 2 PS | BAEJ 2_PS | BAEJ 2_PS_150 | Yes | BAEJ 2_PS_150 | Check if really from Baaj_PS_2 ? how many discharge lines ? if more then 1 split the hydraulic zone. | Baej PS | OPERATOR: Baej PS (line size not given; neighbours on 6in DN150 line) -> BAEJ 2_PS_150. | Confirmed | Operator call | 1 | 669 | 685
458 | Mafraq | Mafraq | Hay Al Mebrek and Hay al ATHAR | BAEJ 2 PS | BAEJ 2_PS | BAEJ 2_PS_150 | Yes | BAEJ 2_PS_150 | Check if really from Baaj_PS_2 ? how many discharge lines ? if more then 1 split the hydraulic zone. | Baej PS, 6" reduced to 2" (DN150->DN50) | OPERATOR: Baej PS, 6in line reduced to 2in (DN150->DN50). BAEJ 2_PS_150. | Confirmed | Operator call | 1 | 672 | 691
459 | Mafraq | Mafraq | BEDAYAT TAREEQ MESHIREF | BAEJ 3 PS | BAEJ 3_PS | BAEJ 3_PS |  | BAEJ 3_PS | To check with operator if realy from Baaj PS 3 ? how many discharge ? | Baej PS, 4" steel line (DN100) | OPERATOR: Baej PS, 4in steel line (DN100). One line -> no split. Keep BAEJ 3_PS. | Confirmed | Operator call | 1 | 667 | 684
460 | Mafraq | Mafraq | Mehrif Hay shamali | BAEJ 3 PS | BAEJ 3_PS | BAEJ 3_PS |  | BAEJ 3_PS | To check with operator if realy from Baaj PS 3 ? how many discharge ? | Meshref PS, 4" steel line (DN100) | OPERATOR: 'Meshref PS', 4in steel line (DN100). Most likely Baej 3 PS (the PS at Meshref road). Keep BAEJ 3_PS - confirm the name. | Confirm | Operator call | 0 | 672 | 700
461 | Mafraq | Mafraq | Hosha | Hosha_Booster | Hosha_Booster_150 | Hosha_Booster_150 |  | Hosha_Booster_150 | Fed by Hosha booster ? or um Lulu ps ? | Hosha Booster | OPERATOR: fed from Hosha Booster (not Um Lulu PS). Keep Hosha_Booster_150. | Confirmed | Operator call | 1 | 619 | 735
462 | Mafraq | Mafraq | Hamnanah , Bostanah and part of Um SWEIneh | Balama PS | Znayah_PS_200 | Znayah_PS_200 |  | Znayah_PS_200 | check if fed by DN200 from Balaama Resv by gravity ? or from Znayah PS_DN200 ? | Znayah PS | OPERATOR: fed from Znayah PS (not Balaama gravity). Keep Znayah_PS_200; line size not given (field note: DN180 + DN300). | Confirmed | Operator call | 1 | 641 | 707
493 | Jarash | Jarash | Hay kalieel | Boidah Ps to resv |  | Bowidah_PS |  | Balela_Resv | To check P_Zone : Balela Reservoir instead of Bowidah_PS |  | Yes - change to Balela Resv (gravity). Bowidah PS pumps to Balela Resv; field: gravity DN100 from DN150 from Balela Resv. Change to Balela_Resv (not in YWC Mafraq layer). | No | Data analysis | 0 | 732 | 883
611 | Irbid | Ramtha | Hay bareed bwaidah | Hosha_Booster |  | Hosha_Booster_200 |  | Hosha_Booster_200 | Fed by Hosha booster or Um Lulu PS ? |  | Hosha Booster (not Um Lulu PS pumps). Um Lulu Resv feeds the booster by gravity DN200, booster DN200 discharge feeds Bwaidha. YWC: 'UM LOLO GRAVITY TO HOSHA BOOSTER'. Keep Hosha_Booster_200. | No | Data analysis | 1 | 562 | 598
612 | Irbid | Ramtha | Hay mesmar | Hosha_Booster |  | Hosha_Booster_200 |  | Hosha_Booster_200 | Fed by Hosha booster or Um Lulu PS ? |  | Hosha Booster (not Um Lulu PS pumps). Um Lulu Resv feeds the booster by gravity DN200, booster DN200 discharge feeds Bwaidha. YWC: 'UM LOLO GRAVITY TO HOSHA BOOSTER'. Keep Hosha_Booster_200. | No | Data analysis | 1 | 558 | 576
613 | Irbid | Ramtha | hay markez sehhi | Hosha_Booster |  | Hosha_Booster_200 |  | Hosha_Booster_200 | Fed by Hosha booster or Um Lulu PS ? |  | Hosha Booster (not Um Lulu PS pumps). Um Lulu Resv feeds the booster by gravity DN200, booster DN200 discharge feeds Bwaidha. YWC: 'UM LOLO GRAVITY TO HOSHA BOOSTER'. Keep Hosha_Booster_200. | No | Data analysis | 1 | 557 | 589
614 | Irbid | Ramtha | Hay sharqi | Hosha_Booster |  | Hosha_Booster_200 |  | Hosha_Booster_200 | Fed by Hosha booster or Um Lulu PS ? |  | Hosha Booster (not Um Lulu PS pumps). Um Lulu Resv feeds the booster by gravity DN200, booster DN200 discharge feeds Bwaidha. YWC: 'UM LOLO GRAVITY TO HOSHA BOOSTER'. Keep Hosha_Booster_200. | No | Data analysis | 1 | 567 | 600
615 | Irbid | Ramtha | Hay karama & sharia' alra'eesi | Hosha_Booster |  | Hosha_Booster_200 |  | Hosha_Booster_200 | Fed by Hosha booster or Um Lulu PS ? |  | Hosha Booster (not Um Lulu PS pumps). Um Lulu Resv feeds the booster by gravity DN200, booster DN200 discharge feeds Bwaidha. YWC: 'UM LOLO GRAVITY TO HOSHA BOOSTER'. Keep Hosha_Booster_200. | No | Data analysis | 1 | 549 | 608
623 | Mafraq | Mafraq | Um_Butaimah | Dogmseh_PS | Dogmseh_PS | Dogmseh_PS |  | Dogmseh_PS | Check if fed from Dogmseh_PS or Bweida_PS | Dogmseh PS, 6" line (DN150) | OPERATOR: fed from Dogmseh PS by 6in (DN150) line. Keep Dogmseh_PS. | Confirmed | Operator call | 1 | 765 | 936
624 | Mafraq | Mafraq | Hweishan | Dogmseh_PS | Dogmseh_PS | Dogmseh_PS |  | Dogmseh_PS | Check if fed from Dogmseh_PS or Bweida_PS | Dogmseh PS, 6" line (DN150) | OPERATOR: fed from Dogmseh PS by 6in (DN150) line (YWC listed Bwaidah PS = origin of water). Keep Dogmseh_PS. | Confirmed | Operator call | 1 | 736 | 882
625 | Mafraq | Mafraq | Ein AL Nabi | Dogmseh_PS | Dogmseh_PS | Dogmseh_PS |  | Dogmseh_PS | Check if fed from Dogmseh_PS or Bweida_PS | Dogmseh PS, 6" line (DN150) | OPERATOR: fed from Dogmseh PS by 6in (DN150) line (YWC listed Bwaidah PS = origin of water). Keep Dogmseh_PS. | Confirmed | Operator call | 1 | 685 | 803
626 | Mafraq | North Badia | Rahmat | Koum Ahmar ps |  | Koum Ahmar_PS |  | Koum Ahmar_PS_100 | How many discharge lines ? split the hydraulic zone |  | Koum Ahmar PS has 2 pumps (50m3/h@250m, 100m3/h@100m) and 2 distribution outlets DN125 + DN100 (field notes). This zone fed by DN100 -> Koum Ahmar_PS_100. Confirm which pump feeds which line. | Confirm | Data analysis | 0 | 694 | 729
630 | Irbid | Irbid | Hay sad | Hosha_Booster |  | Hosha_Booster_200 |  | Hosha_Booster_200 | Fed by Hosha booster or Um Lulu PS ? |  | Hosha Booster (not Um Lulu PS pumps). Um Lulu Resv feeds the booster by gravity DN200, booster DN200 discharge feeds Bwaidha. YWC: 'UM LOLO GRAVITY TO HOSHA BOOSTER'. Keep Hosha_Booster_200. | No | Data analysis | 1 | 564 | 599
654 | Jarash | Jarash | Baleela Hay Almadares | Bowidah Ps to res |  | Bowidah_PS |  | Balela_Resv | To check P_Zone : Balela Reservoir instead of Bowidah_PS |  | Yes - change to Balela Resv (gravity). Bowidah PS pumps to Balela Resv; field: DN150 feeds zone (neighbours fed from Balela Resv). Change to Balela_Resv - confirm the DN150 is the Resv outlet. | Confirm | Data analysis | 0 | 740 | 841
655 | Mafraq | Mafraq | Tareeq Koum Ahmar | Koum ahmar ps | Koum Ahmar_PS | Koum Ahmar_PS_150 | Yes | Koum Ahmar_PS_150 | How many discharge lines ? split the hydraulic zone | Koum Ahmar PS, 6" line (DN150) | OPERATOR: Koum Ahmar PS, 6in line (DN150) -> Koum Ahmar_PS_150. | Confirmed | Operator call | 1 | 676 | 704
656 | Jarash | Jarash | Kabar_BAL | bowidah ps to Res_bal |  | Bowidah_PS |  | Balela_Resv | To check P_Zone : Balela Reservoir instead of Bowidah_PS |  | Yes - change to Balela Resv (gravity). Bowidah PS pumps to Balela Resv; field: fed from Balela Reservoir. Change to Balela_Resv (not in YWC Mafraq layer). | No | Data analysis | 0 | 707 | 777

## Still open
id | Gov | ROU | Sub_zone | Source | P_Zone (before) | P_Zone (now) | P_Zone_changed | P_Zone recommended | Question (To_check) | Operator answer | Final answer (check_answ) | Status | Answer based on | P_zone_ver | Elev_min | Elev_Max
72 | Mafraq | North Badia | Hashmyye/Alyah shwee'er/ Manshiyyet khaleefa /slaah JAW | K140 PS |  | Safawi_PS |  | K140_PS | CHECK the pressure zone - if K140 or Safawi ? are theses two facilities connected ? |  | K140_PS (not Safawi). K140 PS lies inside this zone, Safawi PS ~25 km away. Area tapped DN100/63 on DN400 main from wells K136+K140 (YWC src: wells 136+140, Safawi WS) - same system, pressure from K140 side. | No | Data analysis | 0 | 775 | 820
74 | Mafraq | North Badia | Dir Al-Kahf | Beshryyeh PS |  | Bishiryyah_PS |  | Bishiryyah_PS | TO CHECK IF FROM Beshryyeh PS or Dir Al kahf PS ? |  | Beshryyeh PS - keep Bishiryyah_PS. Field: DN200 from Beshryyeh PS (main filling Dir Al-Kahf tank). Dir Al-Kahf PS sits in this zone (990-1067m) but its pumps H=250m serve upper villages (id75). YWC names Dair Al Kahef PS | Confirm | Data analysis | 0 | 990 | 1067
75 | Mafraq | North Badia | Tal Rmah,Mrajb, deir al qen ,jadaa,Mathnah , mansoora | Dr Al-kahf PS |  | Dir Al-kahf PS |  | Dir Al-kahf PS | Check if the resv Dair Al Qenn is used ? or bypassed ? if used how ? |  | Dair Al Qenn Resv NOT used - bypassed (Master plan: Dir Al-Qun Resv = Abandoned). Fed directly by DN150 from Dir Al-Kahf PS (YWC confirms). YWC has 2 schedules: Tal Rmah / Deir Al Qen+Jadaa+Mathnah+Mansoora | No | Data analysis | 1 | 1071 | 1174
97 | Mafraq | North Badia | Koum Ahmar Hay shamali and Janoobi | Koum Ahmar ps |  | Koum Ahmar_PS |  | Koum Ahmar_PS_125 | How many discharge lines ? split the hydraulic zone |  | Koum Ahmar PS has 2 pumps (50m3/h@250m, 100m3/h@100m) and 2 distribution outlets DN125 + DN100 (field notes). This zone fed by DN125 (+DN100) -> Koum Ahmar_PS_125. Confirm which pump feeds which line. | Confirm | Data analysis | 0 | 696 | 750
98 | Mafraq | North Badia | MANSHIYYET ALKAMEES | Koum Ahmar ps |  | Koum Ahmar_PS |  | Koum Ahmar_PS_100 | How many discharge lines ? split the hydraulic zone |  | Koum Ahmar PS has 2 pumps (50m3/h@250m, 100m3/h@100m) and 2 distribution outlets DN125 + DN100 (field notes). This zone fed by DN100 -> Koum Ahmar_PS_100. Confirm which pump feeds which line. | Confirm | Data analysis | 0 | 727 | 761
99 | Mafraq | North Badia | Rasm Alhesan | Koum Ahmar ps |  | Koum Ahmar_PS |  | Koum Ahmar_PS_100 | How many discharge lines ? split the hydraulic zone |  | Koum Ahmar PS has 2 pumps (50m3/h@250m, 100m3/h@100m) and 2 distribution outlets DN125 + DN100 (field notes). This zone fed by DN100 -> Koum Ahmar_PS_100. Confirm which pump feeds which line. | Confirm | Data analysis | 0 | 744 | 766
100 | Mafraq | North Badia | Hay Al Joulan | Koum Ahmar ps |  | Koum Ahmar_PS |  | Koum Ahmar_PS_100 | How many discharge lines ? split the hydraulic zone |  | Koum Ahmar PS has 2 pumps (50m3/h@250m, 100m3/h@100m) and 2 distribution outlets DN125 + DN100 (field notes). Zone fed by DN100 (+DN50) -> Koum Ahmar_PS_100. GIS network differs - update. | Confirm | Data analysis | 0 | 702 | 720
319 | Mafraq | Mafraq | sahah | Bweidha_Resv_PS |  | Bweidha_Resv_BYPASS |  | Bweidha_Resv_300_G | Check if really they by-pass the reservoir of Bweidha | Not answered | Not answered by operator. All neighbouring Bweidha zones (316-326) confirmed as Bweidha Resv 12in (DN300) line -> most likely Bweidha_Resv_300_G. Ask operator. | Yes | Operator call (blank) | 0 | 815 | 861
418 | Mafraq | Mafraq | Tareeq Al Nahdah | Al Zubaideyeh PS | Al Zubaideyeh_PS | BAEJ_PS_100 | Yes | BAEJ_PS_100 | 2 discharge pipes ? if yes split the hydraulic zone | Baej PS, 4" steel line (DN100) | OPERATOR: NOT Zubaidiyeh PS - fed from Baej PS, 4in steel line (DN100). Confirm Baej 2 or Baej 3, then set BAEJ 2_PS_100 or BAEJ 3_PS. | Confirm | Operator call | 0 | 653 | 680
447 | Mafraq | Mafraq | Hay AGGAD and Balaama Hay shamali | Zeenah PS | Znayah_PS_200 | Znayah_PS_200 |  | Znayah_PS_200 + Balaama_Resv_250_G | check if fed by DN200 from Balaama Resv by gravity ? or from Znayah PS_DN200 ? | Part from Balaama Reservoir, part from Znayah PS | OPERATOR: mixed - part from Balaama Reservoir (gravity), part from Znayah PS. Split polygon: Hay Aggad -> Balaama_Resv_250_G, Balaama Hay Shamali -> Znayah_PS_200. | Split | Operator call | 0 | 650 | 763
460 | Mafraq | Mafraq | Mehrif Hay shamali | BAEJ 3 PS | BAEJ 3_PS | BAEJ 3_PS |  | BAEJ 3_PS | To check with operator if realy from Baaj PS 3 ? how many discharge ? | Meshref PS, 4" steel line (DN100) | OPERATOR: 'Meshref PS', 4in steel line (DN100). Most likely Baej 3 PS (the PS at Meshref road). Keep BAEJ 3_PS - confirm the name. | Confirm | Operator call | 0 | 672 | 700
493 | Jarash | Jarash | Hay kalieel | Boidah Ps to resv |  | Bowidah_PS |  | Balela_Resv | To check P_Zone : Balela Reservoir instead of Bowidah_PS |  | Yes - change to Balela Resv (gravity). Bowidah PS pumps to Balela Resv; field: gravity DN100 from DN150 from Balela Resv. Change to Balela_Resv (not in YWC Mafraq layer). | No | Data analysis | 0 | 732 | 883
611 | Irbid | Ramtha | Hay bareed bwaidah | Hosha_Booster |  | Hosha_Booster_200 |  | Hosha_Booster_200 | Fed by Hosha booster or Um Lulu PS ? |  | Hosha Booster (not Um Lulu PS pumps). Um Lulu Resv feeds the booster by gravity DN200, booster DN200 discharge feeds Bwaidha. YWC: 'UM LOLO GRAVITY TO HOSHA BOOSTER'. Keep Hosha_Booster_200. | No | Data analysis | 1 | 562 | 598
612 | Irbid | Ramtha | Hay mesmar | Hosha_Booster |  | Hosha_Booster_200 |  | Hosha_Booster_200 | Fed by Hosha booster or Um Lulu PS ? |  | Hosha Booster (not Um Lulu PS pumps). Um Lulu Resv feeds the booster by gravity DN200, booster DN200 discharge feeds Bwaidha. YWC: 'UM LOLO GRAVITY TO HOSHA BOOSTER'. Keep Hosha_Booster_200. | No | Data analysis | 1 | 558 | 576
613 | Irbid | Ramtha | hay markez sehhi | Hosha_Booster |  | Hosha_Booster_200 |  | Hosha_Booster_200 | Fed by Hosha booster or Um Lulu PS ? |  | Hosha Booster (not Um Lulu PS pumps). Um Lulu Resv feeds the booster by gravity DN200, booster DN200 discharge feeds Bwaidha. YWC: 'UM LOLO GRAVITY TO HOSHA BOOSTER'. Keep Hosha_Booster_200. | No | Data analysis | 1 | 557 | 589
614 | Irbid | Ramtha | Hay sharqi | Hosha_Booster |  | Hosha_Booster_200 |  | Hosha_Booster_200 | Fed by Hosha booster or Um Lulu PS ? |  | Hosha Booster (not Um Lulu PS pumps). Um Lulu Resv feeds the booster by gravity DN200, booster DN200 discharge feeds Bwaidha. YWC: 'UM LOLO GRAVITY TO HOSHA BOOSTER'. Keep Hosha_Booster_200. | No | Data analysis | 1 | 567 | 600
615 | Irbid | Ramtha | Hay karama & sharia' alra'eesi | Hosha_Booster |  | Hosha_Booster_200 |  | Hosha_Booster_200 | Fed by Hosha booster or Um Lulu PS ? |  | Hosha Booster (not Um Lulu PS pumps). Um Lulu Resv feeds the booster by gravity DN200, booster DN200 discharge feeds Bwaidha. YWC: 'UM LOLO GRAVITY TO HOSHA BOOSTER'. Keep Hosha_Booster_200. | No | Data analysis | 1 | 549 | 608
626 | Mafraq | North Badia | Rahmat | Koum Ahmar ps |  | Koum Ahmar_PS |  | Koum Ahmar_PS_100 | How many discharge lines ? split the hydraulic zone |  | Koum Ahmar PS has 2 pumps (50m3/h@250m, 100m3/h@100m) and 2 distribution outlets DN125 + DN100 (field notes). This zone fed by DN100 -> Koum Ahmar_PS_100. Confirm which pump feeds which line. | Confirm | Data analysis | 0 | 694 | 729
630 | Irbid | Irbid | Hay sad | Hosha_Booster |  | Hosha_Booster_200 |  | Hosha_Booster_200 | Fed by Hosha booster or Um Lulu PS ? |  | Hosha Booster (not Um Lulu PS pumps). Um Lulu Resv feeds the booster by gravity DN200, booster DN200 discharge feeds Bwaidha. YWC: 'UM LOLO GRAVITY TO HOSHA BOOSTER'. Keep Hosha_Booster_200. | No | Data analysis | 1 | 564 | 599
654 | Jarash | Jarash | Baleela Hay Almadares | Bowidah Ps to res |  | Bowidah_PS |  | Balela_Resv | To check P_Zone : Balela Reservoir instead of Bowidah_PS |  | Yes - change to Balela Resv (gravity). Bowidah PS pumps to Balela Resv; field: DN150 feeds zone (neighbours fed from Balela Resv). Change to Balela_Resv - confirm the DN150 is the Resv outlet. | Confirm | Data analysis | 0 | 740 | 841
656 | Jarash | Jarash | Kabar_BAL | bowidah ps to Res_bal |  | Bowidah_PS |  | Balela_Resv | To check P_Zone : Balela Reservoir instead of Bowidah_PS |  | Yes - change to Balela Resv (gravity). Bowidah PS pumps to Balela Resv; field: fed from Balela Reservoir. Change to Balela_Resv (not in YWC Mafraq layer). | No | Data analysis | 0 | 707 | 777

## Legend
Status | Meaning | Count
Confirmed | Confirmed by operator call - P_Zone updated, P_zone_ver = 1 | 48
Confirm | Answer given, but one detail still needs operator confirmation | 9
Split | Operator confirmed mixed supply - polygon needs to be split | 1
Yes | Not answered yet - ask operator | 1
No | Answered from data (field notes, YWC layer, master plan) - not covered by the operator call | 10